## Slide 1: Categorization and Classification of SSCs for a Current Generation Nuclear Power Plant Using a RIPB Advanced Reactor Standard
PSAM 16
June, 2022
Honolulu, Hawaii
Applied Reliability Engineering, Inc
Dave Blanchard
dblanchard@ar-eng.com

## Slide 2: Categorization and Classification of SSCs for a Current Generation Nuclear Power Plant Using a RIPB Advanced Reactor Standard
Motivation for this evaluation
  ANS/ANSI 30.3* is a recently completed RIPB advanced light water reactor design standard that has received public review and comment, was recently balloted and approved and is expected to be published in 2022.
  During its development, its guidance was tested as one means of ensuring its ability to be implemented.
  A current generation plant PRA was used as a part of this testing to address what might have been classified as Safety Related had insights from the PRA been available at the time that it was licensed.
*ANS/ANSI 30.3-202x, ‘Light Water Reactor Risk-Informed Performance-Based Design’

## Slide 3: Categorization and Classification of SSCs for a Current Generation Nuclear Power Plant Using a RIPB Advanced Reactor Standard
Outline
ANS/ANSI 30.3-202x
‘Light Water Reactor Risk-Informed Performance-Based Design’
Top Level Criteria & Definition of Plant Capability Defense in Depth and Risk Significance
Description of PWR reviewed against ANS/ANSI 30.3
Classification results (deterministic)
Categorization results (probabilistic)
Summary

## Slide 4: ANSI/ANS 30.3 – Table of Contents
Purpose and scope
Acronyms and Definitions
Nuclear Reactor Design Process
Safety Requirements and Functions
Licensing Basis Event Identification
Design Basis Safety Analysis
Probabilistic Risk Assessment
Severe Accident Considerations
Classification and Categorization of Systems, Structures and Components
Systematic Defense-in-Depth
Performance Based Decisionmaking
References

## Slide 5: ANS/ANSI 30.3 – Licensing Basis Event Identification
ANS/ANSI 30.3 provides flexibility in the development of licensing basis events
Acceptable approaches encompass the following spectrum:
  Traditional deterministic approach supplemented by information from the PRA
    Blend of deterministic/probabilistic methods in between
  Beginning with the accident sequences of the PRA, identifying those most important to risk and adjusting them to reflect deterministic defense-in-depth considerations

## Slide 6: ANS/ANSI 30.3 – Classification
Classification is deterministic in ANS/ANSI 30.3
  Objective is to place SSCs into three classes
    Safety related
    Non safety related (with special treatment requirements)
    Non safety (no special treatment requirements)
  Endorses classification guidance of ANS/ANSI 58.14-2011
  ‘Safety and pressure integrity classification criteria for light water reactors’
  Note: ANS/ANSI 58.14 is a deterministic standard that
  was not developed to be RIPB
  (However, see footnote on bottom of next slide)
SR
NSR
Lo Risk
Hi Risk

## Slide 7: ANS/ANSI 30.3
SSC classification guidance of ANS/ANSI 58.14-2011
  Safety Related
    Applies to a function, SSC, or part that is relied upon during or following a DBE to ensure any of the three functions
      Primary system integrity
      Shutdown the reactor and maintain safe shutdown
      Limit releases
  Relied upon*
    for DBEs: the SSCs that are necessary and sufficient (i.e., the minimal subset of SSCs) to assure each of the three basic safety-related functions in the presence of a postulated single failure plus any other coincident occurrence assumed in the safety analysis;
    for special events: the SSCs that are nec- essary and sufficient (i.e., the minimal sub- set of SSCs) to assure required functions in the presence of postulated failures (e.g., common cause) related to the specific special event.
*The definition of ‘relied upon’ allows the use of fault tree analysis methods to identify SSCs that are candidates for classification as SR.

## Slide 8: ANS/ANSI 30.3 - Categorization
Categorization brings in risk metrics
and applies performance based criteria
  No specific thresholds are endorsed for high and low risk significance
  The designer is allowed flexibility in defining what is meant by ‘risk significant’
  A final sensitivity study is used as a basis to demonstrate the effectiveness of the selected SSCs in managing risk
    The selected SSCs consist of those identified as SR and NSRST during classification and risk significant as a part of categorization
SR
NSR
Lo Risk
Hi Risk

## Slide 9: ANS/ANSI 30.3 - Categorization
Characteristics of the risk significance sensitivity study
  The analysis shall use conservative failure assumptions for SSCs categorized as not safety significant. Such conservative assumptions may range across the following spectrum:
    No preventive or mitigative credit is taken for SSCs that are not risk significant (e.g., these SSCs are assumed failed).
    Failure probabilities are assigned to SSCs that are not risk significant for which their performance shall be monitored in a reliability assurance program and corrective actions taken if the performance criteria are not met.
  An engineering rationale for the risk significance categorization of each SSC shall be developed and documented.
  The designer is allowed to raise or lower initial classification and categorization results based on the outcome of the final sensitivity analysis accompanied by development of an engineering rationale justifying the change.

## Slide 10: Top Level Criteria & Definition of Plant Capability Defense in Depth and Risk Significance
Select a high level measure that reflects effective protection of public health & safety (e.g.,):
  One or more of the three basic safety functions
    Primary system integrity
    Shutdown reactor and maintain safe shutdown
    Limit releases
  Frequency-consequence curve
Plant Capability Defense in Depth
  Identify SSCs necessary to meet deterministic criteria of ANS/ANSI 58.14
  Add SSCs useful in meeting (and providing margin on) risk significance criteria
Risk significance
  Identify SSCs necessary to meet risk criteria for selected metric(s)
  Add SSCs useful in meeting (and providing margin on) risk significance criteria
ANS/ANSI 30.3 gives the designer the flexibility of identifying the specific metrics to be used to define safety
}

## Slide 11: Current Generation PWR Characteristics
Began operation early 1970s
3 train AFW
2 train HPSI/LPSI
2 division Emergency AC
Internal fire, flood and external event related SSCs are credited in the internal events PRA
Application of ANS/ANSI 30.3:
Use Core Damage Frequency for internal events PRA as surrogate for Shutdown reactor and maintain safe shutdown safety function
Quantitative safety goal as criterion for this safety function (1E-4/yr)
Chart: 
| LOCA, inj failure | LOCA, recirc failure | SGTR | Transient, w/o 2nd cooling, no F&B | ATWS | Residual
CDF | 0.55067 | 0.13382 | 0.12817 | 0.16891 | 0.010804 | 0.0076249
Baseline CDF = 6E-6/yr

## Slide 12: Classification Implement ANS/ANSI 58.14 deterministic criteria using the PRA logic models
Relied upon
  “…SSCs that are necessary and sufficient (i.e., the minimal subset of SSCs) to assure each of the three basic safety-related functions in the presence of a postulated single failure…”
SSCs that are candidates for classification as Safety Related can be identified directly from the fault trees and cut sets of the PRA.
In this presentation, the definition of ‘relied upon’ was implemented using the PRA by applying a method known as Top Event Prevention Analysis.

## Slide 13: Top Event Prevention Analysis Concepts and Definitions
Prevention Analysis
Top of fault tree or any Boolean expression
Combination of events that will prevent the occurrence of the Top Event
Desired number of events in each cut set that, if prevented, will preclude the occurrence of the Top Event
Basic events that are to be credited toward the prevention of the Top Event
Basic events that are not credited toward the prevention of the Top Event
Top Event
Prevention Sets
Prevention Level
Credited Events
Excluded Events
Fault Tree Analysis
Top of fault tree or any Boolean expression
Combination of events that will result in the failure represented by the Top Event
Desired probability or order which makes each cutset insignificant
Top Event
Cut Sets
Truncation Level

## Slide 14: Top Event Prevention Analysis: Simple Example
Minimal Level 2 Prevention Sets
N * A * C1 +
N * A * C2 * SW +
N * A * C3 * SW.
Top Event
  N * A +
  N * C1 * SW +
N * C1 * C2 * C3.
Top Event
Compressors
Air
Receivers
Air Dryer
N
2
C2
C3
A
C1
Fussell-Vesely
Risk Achievement Worth
N
A
C1
C2
C3
1.0
~1.0
10-3
10-3
10-3
104
103
1.2
1.1
1.1
N
-4
10
-3
10
-2
10
A
C1
C2
C2
-2
10
10 N * A
10 N * C1 * SW
10 N * C1 * C2 * C3
-10
-7
Prevention Sets
Level 2
(N*A) *
(N*C1 + N*SW + C1*SW ) *
(N*C1 + N*C2 + N*C3 +
C1*C2 + C1*C3 + C2*C3 ).
SW
-4
10
C3
SW
-2
10
-4
10
SW
C3
-10
SW
10-3
10
Importance measures
Prevention analysis
Notes: 4

## Slide 15: Classification (1st iteration) Application of ANS/ANSI 58.14 deterministic criteria
Build and solve model for core damage
  >600,000 cut sets (modularization, truncation 1E-14/yr)
Define Prevention Level (deterministic)
  Level 2 prevention (to meet the definition for ‘relied upon’ in ANS/ANSI 58.14)
For each cut set, generate expression that represents prevention by selected criteria
  Credited events
  Excluded events – Examples
  Initiating Events
  SSCs with marginal reliability (e.g., RVs challenged to relieve water)
  Selected Operator actions
  short time frames/high stress
  moderate to high conditional actions
Form Boolean product
  Expand
  Simplify (>1E9 prevention sets)
  (up to 770 basic events in length)

## Slide 16: Classification (1st iteration) Application of ANS/ANSI 58.14 deterministic criteria – Example Results
Example candidates for classification as Safety Related
AFW
  3 trains needed to meet single failure criterion
HPSI/LPSI
  2 trains
  incl op actions to align recirc
AC power/DC power
  Both emergency diesels
  Offsite power
  One division of DC
Instrument air
  SGTR needs isolation of affected SG which requires instrument air
Example candidates for classification as non Safety Related
BOP SSCs
AC power/DC power
  Switchyard components
  Selected 2400v, 480v buses
  One division of DC
Main steam line isolation
Feed & Bleed support
  PORVs
  Incl op action to initiate F&B
Special events
  Blackout EDG
  App R, NFPA-805 equipment (e.g., hot shutdown panel)
  FLEX equipment

## Slide 17: Categorization (1st iteration) Testing the effectiveness of deterministically selected SSCs on risk
Set all events that are not selected using the deterministic criteria to True.
CDF rises multiple orders of magnitude
  99% if the increase comes from the highest frequency initiating events
    Manual shutdown
    Turbine trip
    Very small LOCA
    Loss of feedwater
    Loss of main condenser
    Loss of offsite power
Revise the deterministic criteria to require three failures for the above high frequency events (Level 3 prevention)

## Slide 18: Classification (2nd iteration) Application of ANS/ANSI 58.14 deterministic criteria
Build and solve model for core damage
  >600,000 cut sets (modularization, truncation 1E-14/yr) – same as 1st iteration
Define Prevention Level (deterministic)
  Level 3 prevention for high frequency initiating events (exceeds 58.14 criterion)
  Level 2 prevention (to meet the definition for ‘relied upon’ in ANS/ANSI 58.14)
For each cut set, generate expression that represents prevention by selected criteria
  Credited events
  Excluded events – same as 1st iteration
Form Boolean product
  Expand
  Simplify (~7E6 prevention sets)
  (up to 870 basic events in length)

## Slide 19: Categorization (2nd iteration) Testing the effectiveness of deterministically selected SSCs on risk
Set all events that are not selected using the revised deterministic criteria to True.
CDF is slightly greater than risk criterion (1E-4/yr)
Identify SSCs dominating the residual risk increase using importance measure (e.g., Fussell-Vesely)
  ~2 dozen basic event (or modules) identified that return the CDF to within the risk criterion with margin
    A number of operator recovery actions (e.g., alignment of blackout diesel)
    Charging components affecting makeup and pressurizer level control
    Additional instrument air trains

## Slide 20: Selected examples of application of blending deterministic and risk criteria to the PRA
AFW
  3 trains needed
HPSI/LPSI
  2 trains
  incl op actions to align recirc
AC power/DC power
  Both emergency diesels
  Swyd comp supporting emergency buses
  Blackout diesel
  Both DC divisions
Example candidates for classification as non Safety Related
BOP SSCs
Main steam line isolation
Special events
  App R, NFPA-805 equipment
  (e.g., hot shutdown panel)
  FLEX equipment
Instrument air
  SGTR needs isolation of affected SG
  Backup to SR pneumatic supplies for ECCS valves
Feed & Bleed support
  PORVs
  Incl op action initiate F&B
Example candidates for classification as Safety Related or non Safety Related with special treatment requirements

## Slide 21: ANS/ANSI 30.3 Sensitivity Study Results
Baseline CDF crediting all SSCs modeled in the PRA - 6E-6/yr
CDF crediting only SSC candidates for classification as SR or NSRST - 3E-5/yr
Chart: 
| LOCA, inj failure | LOCA, rec failure | SGTR | Trans, no 2nd cooling, no F&B inj | Trans, no 2nd cooling, no F&B rec | ATWS | Residual | Residual
 | 0.19543 | 0.27589 | 0.13669 | 0.29103 | 0.04473 | 0.01349 | 0.03873 | 0.00402
Chart: 
| LOCA, inj failure | LOCA, recirc failure | SGTR | Transient, w/o 2nd cooling, no F&B | ATWS | Residual
CDF | 0.55067 | 0.13382 | 0.12817 | 0.16891 | 0.010804 | 0.0076249

## Slide 22: ANS/ANSI 30.3 Sensitivity Study Results
Why is a factor of 5 increase acceptable when crediting only SSCs that are SR or NSRST?
  Margin remains on the risk criteria in which other events (e.g., earthquakes, internal fires and floods) can be accommodated.
  Risk informed guidance, such as NEI 00-04, suggests that common cause events having a Risk Achievement Worth less than 20 need not be considered risk significant. In this evaluation, multiple entire systems collectively are assumed not to perform their functions resulting in a factor of three less than the CCF risk significance guidance of NEI 00-04.

## Slide 23: Summary
ANS/ANSI 30.3 provides practical and flexible guidance in the classification and categorization of SSCs that is performance based.
The logic models of the PRA can be used
Deterministically to identify a subset of SSCs that meet the deterministic defense in depth criterion of ANS/ANSI 58.14, e.g.,
  Identify a minimal set of SSCs that should be candidates for classification as Safety Related
Probabilistically to identify those SSCs collectively effective in managing safety, e.g.,
  Provide margin on meeting established risk criteria
  Identify additional SSCs that may be candidates for classification as non Safety Related but require attention with special treatment or in a reliability assurance program

## Slide 24: Categorization and Classification of SSCs for a Current Generation Nuclear Power Plant Using a RIPB Advanced Reactor Standard
Next steps…

## Slide 25
Backup slides…

## Slide 26: Risk-Informed Performance-Based (from SRM to SECY 98-144)
A risk-informed approach enhances the deterministic approach by:
  allowing explicit consideration of a broader set of potential challenges to safety,
  providing a logical means for prioritizing these challenges based on risk significance, operating experience, and/or engineering judgment,
  facilitating consideration of a broader set of resources to defend against these challenges,
  explicitly identifying and quantifying sources of uncertainty in the analysis (although such analyses do not necessarily reflect all important sources of uncertainty), and
  leading to better decision-making by providing a means to test the sensitivity of the results to key assumptions.

## Slide 27: Risk-Informed Performance-Based (from SRM to SECY 98-144)
A performance based approach relies upon:
  measurable (or calculable) outcomes (i.e., performance results) to be met, but provides more flexibility to the licensee as to the means of meeting those outcomes.
  establishes performance and results as the primary basis for regulatory decision-making, and
  incorporates the following attributes:
    measurable (or calculable) parameters (i.e., direct measurement of the physical parameter of interest or of related parameters that can be used to calculate the parameter of interest) exist to monitor system, including facility and licensee , performance,
    objective criteria to assess performance are established based on risk insights, deterministic analyses and/or performance history,
    licensees have flexibility to determine how to meet the established performance criteria in ways that will encourage and reward improved outcomes; and
    a framework exists in which the failure to meet a performance criterion, while undesirable, will not in and of itself constitute or result in an immediate safety concern.

## Slide 28: RIPB Categorization and Classification References
Standards
ANS/ANSI 30.3 ‘Light Water Reactor Risk-Informed Performance-Based Design’
ANS/ANSI 58.14 ‘Safety and pressure integrity classification criteria for light water reactors’
ANS/ANSI 53.1 ‘nuclear safety design process for modular helium-cooled reactor plants’
ANS/ANSI 54.1 ‘Nuclear Safety Criteria and Design Process for Sodium Fast Reactor Nuclear Power Plants’
Methods
NEI 18-04 ‘Risk-Informed Performance-Based Technology Inclusive Guidance for Non-Light Water Reactor Licensing Basis Development’
NEI 00-04 ‘10 CFR 50.69 SSC Categorization Guideline’

## Slide 29: RIPB Categorization and Classification References
Top Event Prevention Analysis
‘Top Event Prevention in Complex Systems’, Proceedings of the 1995 Joint ASME/JSME Pressure Vessels and Piping Conference, June 1995
‘Top Event Prevention Analysis, A Deterministic Use of PRA’, Proceedings of the International KNS/ANS Topical Meeting on PSA, 1995.
‘Risk-Informed Physical Security; Dynamic Allocation of Resources’, Proceedings of PSA '05, Sep 2005
EPRI 1019183 ‘Effects of Digital I&C Defense-in-Depth and Diversity on Risk in Nuclear Power Plants’, December 2009.
‘Risk Informed Safety Margin Characterization Case Study: Selection of Electrical Equipment To Be Subjected to Environmental Qualification’, INL/EXT-11-23479 Rev. 1, April 2012
‘HAZCADS – Hazard Analysis and Consequence Analysis of Digital Systems’, EPRI 3002012755, December 2018