## Slide 1: Significance Determination Process
Notes: Right-click, select Format Background and change the Picture fill, File

## Slide 2: Significance Determination Process (SDP)
process for determining the safety or security significance of events or issues at nuclear power plants
Given a functional degradation over a period of time, the SDP can be used to determine the increase in risk (Core Damage Frequency or Large Early Release Frequency) for postulated initiating events
Part of the Reactor Oversight Framework

## Slide 3: Significance Determination Process
The SDP assigns a colour to the events
  Green: Very low safety significance CDF < 1E-6
  White: Low to moderate safety significance 1E-6 < CDF < 1E-5
  Yellow: Substantial safety significance 1E-5 < CDF < 1E-4
  Red: High safety significance 1E-4 < CDF
Purpose and scope

## Slide 4: Significance Determination Process
Phase 1 – Definition and Initial Screening of Findings (table)
  Characterization of the event
  Initial Screening Out of Low-Significant Issues
Phase 2 – quantify impact using (normally) simplified risk models
  Performed by event analyst
  Study:
    Initiating events
    Which systems/functions are affected – defining the sequence
    Exposure time
  A simplified result is generated
Phase 3 – if detailed justification needed
  Detailed justification needed
  Risk analyst performs justification
Overview of process

## Slide 5: The process
Create/import Original Event
Filter the event with simple rules
No SDP
Filtered out
May imply risk
SDP phase 2: Easy evaluation of impact using PSA
Type of impact, system, duration
Colour
ΔCDF / ΔLERF
If further assessment deemed necessary
SDP phase 3: impact using standard PSA
Colour
ΔCDF / ΔLERF
No risk
SDP event: Add information
SDP phase 1:
Identification and impact
Green
Create SDP Event

## Slide 6: RiskSpectrum SDP

## Slide 7: RiskSpectrum SDP
Risk Monitor
  Tool for planning and monitoring risk in plant operations
SDP
  Process for analysing and determining the significance of events that has occured
Difference risk monitor & SDP tool
Notes: 40 min for Ola. Maybe 30 min for me?

## Slide 8: The process in RiskSpectrum SDP
Filtering questions defined by you
Answers will either be screened out or create an SDP event
Create and filter the original event

## Slide 9: The process in RiskSpectrum SDP
Add more information about the event
If an SDP event – follow the guide

## Slide 10: The process in RiskSpectrum SDP
  Initiating Event
  Mitigation System
  Barrier Integrity
SDP Phase 1 - select impact

## Slide 11: The process in RiskSpectrum SDP
Initiating event
Unavailability over time period
SDP Phase 2 - Define type of impact

## Slide 12: The process in RiskSpectrum SDP
Select affected equipment
SDP Phase 2 – Set degradation if selected

## Slide 13: The process in RiskSpectrum SDP
Set the type of failure:
  Human error
  Component
  Management
SDP Phase 2 – Run analysis

## Slide 14: The process in RiskSpectrum SDP
The PSA model is run, with the conditions defined
Impact assessed – in this case Green
SDP Phase 2 – Run analysis

## Slide 15: RiskSpectrum SDP
When approved the events appears on the summary
You can drill down in the report to look into the analysis
Submit report for review

## Slide 16: RiskSpectrum SDP
Manage several stations/units
Using the PSA model
  You can use any RiskSpectrum PSA model you would like - configurable
Reports and result overview (dashboards)
Key features

## Slide 17: RiskSpectrum SDP
Manage several stations/units
Using the PSA model
  You can use any RiskSpectrum PSA model you would like - configurable
Reports and result overview (dashboards)
User management system
Review and approve
Process control/overview
Browser based system
Key features

## Slide 18: RiskSpectrum SDP
Dashboard for all events reported
  Manage several plants and units
Provides tool assistance for the steps in the SDP process
Configurable for your needs, e.g., any language
Easy to use interface, based on real PSA model to estimate risk
User management system with different user rights
Conclusions

## Slide 19: Thank you
Please contact:
Johan Sörman +46 70 773 0404
Johan.sorman@lr.org