## Slide 1: Conditional Quantification PSAM 16
Ola Bäckström Pavel Krcal Pengbo Wang

## Slide 2: Outline of this presentation
Problem statement
Conditional quantification basics
The implementation in RiskSpectrum
Future
Conclusions

## Slide 3: Problem statement
There is a need for conditional quantification in PSA
Current methods include:
  CCF approaches
  Post processing
  Explicit modelling
Drawbacks:
  Cut off issues
  Use of separate events (e.g. CCF, HFE dependency) distorts importance and potentially uncertainty.

## Slide 4: Conditional quantification, basics
P(A) = P(A|B)·P(B) + P(A|-B)·(1-P(B))
  P(A|-B) = [P(A) – P(A|B)·P(B)]/(1-P(B))
  Hence, success of B should decrease the probability of A
How is this considered in our PSAs today? Compare:
  CCF calculation approaches – in which the independent failure (not conditional failure of “B”) is reduced [Considered]
  HFE dependency – in which success is not considered [Disregarded]

## Slide 5: Conditional quantification, basics
P(A) = P(A|B)·P(B) + P(A|-B)·(1-P(B))
  P(A|-B) = [P(A) – P(A|B)·P(B)]/(1-P(B))
  Hence, success of B should decrease the probability of A
HFE dependency estimates
  A conservative approach – the aim is to avoid an undeserved credit
  Accounting for success could lead to overly optimistic results
  Example: complete dependency – does success mean the dependent failure is impossible?

## Slide 6: RiskSpectrum PSA implementation
Calculate probabilities based on rules
  Rules are applied during MCS generation
Conditional Quantification

## Slide 7: RiskSpectrum PSA implementation
Calculate probabilities based on rules
  Rules are applied during MCS generation
Application areas:
  HRA (focus area)
    No decrease at success
Conditional Quantification
Ex. HRA dependency levels:
High P’(A) = ( 1+P(A) ) / 2
Medium P’(A) = ( 1+6P(A) ) / 7
Low P’(A) = ( 1+19P(A) ) / 20
When the Dependent Event is found in a MCS …
…together with the conditional event(s)…
The dependent event is calculated as…

## Slide 8: RiskSpectrum PSA implementation
Calculate probabilities based on rules
  Rules are applied during MCS generation
Application areas:
  HRA (focus area)
  CCF
  Any calculations including
  conditions
Conditional Quantification

## Slide 9: Results and importance
MCS list contains “same” event, but of different value (shadow events A’ )
Traceability:
  Right-click in the result grid – a jump to the conditional probability used in quantification
  MCS Editor – conditional probability number displayed

## Slide 10: Results and importance
MCS list contains “same” event, but of different value (shadow events A’ )
Importance is improved as it considers all event “A” and its shadow events (A’)
  FV(A) = Q(cutset contains A or any A’) / Q(all),
  RIF(A) = Q(A = 1, and all A’ = 1) / Q(all),
  RDF(A) = Q(all) / Q(A=0, and all A’=0).

## Slide 11: RiskSpectrum PSA future
Include possibility to select success management
  More flexible definition of CCF models
Will be a generic framework for management of conditional quantification in PSA

## Slide 12: Conclusion
Existing methods for inclusion of conditional probabilities have drawbacks (e.g. post processing and CCF)
A generic framework for conditional probabilities has been developed and implemented
  Currently with focus to manage HFE dependency (to not consider success)
  Further development is to manage also success

## Slide 13: Thank you - Questions
Please contact:
Ola Backstrom or Pavel Krcal
Ola.backstrom@lr.org