## Slide 1
Global Expertise • One Voice
Mike Powell (PWROG Chairman)
Flex Equipment Reliability Data

## Slide 2: Topics
Why Develop Failure Rates
Component Scope and Boundaries
Data Collection
Insights from Data Review
Results
Conclusion

## Slide 3
Why Collect Data
Flex was a significant investment for all sites
  Want to leverage investment to maximize safety benefits and improve margin
RG 1.160 Expands the use of Flex in the EOPs without additional burden associated inclusion in Mrule Scope
  Can provide significant safety benefit for crediting Flex in areas
  Can be significant reduction in CDF
  Improved MSPI Margin
  Use in SDPs
Modeling Requires Failure rates

## Slide 4
Component Scope and Boundaries
PWROG/BWROG Team
  Reviewed what equipment was being added to PRA models
  Defined component boundaries

## Slide 5
Component Scope and Boundaries
Component Type | Boundary
Portable Diesel Generator | Diesel engine with all components in the exhaust path Electrical generator Generator exciter Combustion air Lube oil systems Fuel oil systems and starting compressed air system Local instrumentation and control circuitry Starter batteries
Portable Combustion Turbine | Gas turbine Generator Circuit breaker Local lubrication or cooling systems Local instrumentation and control circuitry Starter batteries
Portable Diesel-Driven Pump | Pump Diesel engine Local lubrication or cooling systems Local instrumentation and control circuitry Starter batteries

## Slide 6
Component Scope and Boundaries
Component Type | Boundary
Portable Motor-Driven Positive Displacement Pump | Pump Motor Local circuit breaker Local lubrication or cooling systems local instrumentation and control circuitry
Portable Diesel-Driven or Motor-Driven Air Compressor | Compressor Driver Local circuit breaker Local lubrication or cooling systems Local instrumentation and control circuitry Starter batteries

## Slide 7
Data Requested from all US Plants
National SAFER Response Center
  Equipment is not modeled in PRA due to current PRA mission time (24 hours)
  Large source of data for similar components that are modeled
  Components with same manufacturer, make and model number as equipment located at any US Site
    Equipment was modified for transportability
      Needs to be evaluated, along with Maintenance Practices to determine if data can be combined with site data (future effort)
Data Collection

## Slide 8: Data Collection – Demand/Run Hours
Using Estimated values
Based on PM/Test frequencies and minimum run durations specified
    Operational data for other uses considered if reported

## Slide 9: Data Collection – Failures
  Need consistent failure definitions
    Utilities provided reports of any adverse condition (provides available documentation of condition)
    Data evaluation team review determines failure

## Slide 10: Insights from Data Review
  Failure Definitions
    Limited run hours available for run times > 1 hour
    Modified failure definitions:
    Failure to Start:
      Fails to start on first attempt with limited credit for second attempt without diagnoses
    DG Failure to Load/Run:
      Not Used
    Failure to Run:
      Failure after success start – no minimum run time

## Slide 11
Insights from Data Review
  Failure Reporting
    Utilities have very low reporting thresholds
    100’s to 100’s of Flex related Condition Reports
    Handful of potential equipment failures
    Very few failures
    Need to develop a screening process for future updates
  Maintenance Strategies
    Different Maintenance Strategies impact classification of failures
      (e.g., battery trickle charger versus battery testing)
    Final report will have options for failure rates based on different maintenance strategies

## Slide 12
Results
Chart: Figure 1: Flex Failure Probabilities
| Portable Diesel Generator | Portable Combustion Turbine | Portable Diesel-Driven Pump | Portable Motor-Driven Positive Displacement Pump | Portable Diesel-Driven or Motor-Driven Air Compressor
Fail to Start | 0.0435 | 0.033 | 0.0338 | 0.00735 | 0.0246
Fail to Run 24 hours | 0.2472 | 0.4464 | 0.372 | 0.3744 | 0.6768

## Slide 13
Conclusions
  Improvements to the process used for sites to provide data is needed
    Failure definitions to be used by the sites to screen events as potential
  Sites use different maintenance strategies for their Flex equipment
    This should be accounted for by a plant specific Bayesian update
  Personnel providing the demand and run data need a good understanding of how the data was entered into the EPRI PM database
    High turnover rate of Flex maintenance/program owners has complicated obtaining the correct data.

## Slide 14
Conclusions
  Due to the sparse data, component groups were combined
    As more data becomes available, the component groups may change
  It was originally planned to include data from the 2 SAFER centers
    Equipment at the SAFER was modified to allow for air transport to the sites
    Evaluation of the impact of these changes and whether the equipment can be pooled with site equipment will be evaluated in the next update
  It is expected that with additional data (primarily run hours), failure rates will improve