## Slide 1: Assessing the Impact of Combined External Events on the Safety of NPP Paks
Tamas Siklossy, Attila Bareith, Bence Burjan, Barnabas Toth
PSAM16
Honolulu, Hawaii, USA, June 26 – July 1, 2022
siklossyt@nubiki.hu

## Slide 2: Content
  Introduction
  Objectives
  Types of External Hazard Combinations
  Major Analysis Steps
  Findings
  Conclusions

## Slide 3: Introduction
  Mostly single external hazards were considered in the definition of the design basis for the Paks NPP in Hungary
  Motivation of assessing the impact of hazard combinations on NPP safety
    Hungarian Nuclear Safety Codes and international recommendations
    Lessons learnt from the Fukusima Dai-ichi accident
    Finding of the Periodic Safety Review of the Paks NPP in 2017
  Preparatory study in 2018:
    the regulations and recommendations have been looked at
    the available methodologies have been studied and evaluated
    analysis practices applied in Hungary have been reviewed
    a proposal has been developed for the technical tasks and the schedule thereof to identify combinations of external hazards and assess the effects of such hazards on NPP safety (including high level methodology of each analysis steps)

## Slide 4: Objectives
  Identify combinations of external hazards and assess the effects of such combinations on NPP safety
    identification and characterization of load combinations
    assess the effects of hazard combinations on NPP safety:
      justification of the adequacy of protection against hazard combinations to be included in the design basis
      quantification of the residual risk due to beyond design basis load combinations and identification of the main risk contributors
  Identify important safety concerns
  Transients in full power operation and in LPSD states

## Slide 5: Types of Combined External Hazards
  Combination of dependent hazards – causal connection
    Consequential hazards – cause-effect relation:
      A may cause B (e.g. explosion – forest fire)
      A is a prerequisite of B (e.g. earthquake – soil liquefaction)
    Non-consequential connected hazards (correlated hazards) – common root cause (e.g. a meteorological condition triggers many hazards)
  Combination of independent hazards (coincidental hazards) – no causal connection
    independent events have a high occurrence frequency,
    at least one of the events is long-lasting and usually rare.

## Slide 6: Major Analysis Steps
PSA:
Selection of combined external hazards
Screening of combined external hazards
Detailed assessment of screened-in event combinations:
  Hazard assessment
  Plant response and fragility analysis
  Event logic modeling and risk quantification
Design basis (identification and justification of protection):
Selection of combined external hazards
Screening of combined external hazards
Definition of design basis load combinations
Evaluation of plant protection and specification of protective measures

## Slide 7: Selection of Combined External Hazards
  Development of a comprehensive list of potential single external hazards
  Screening of single hazards with respect to hazard combinations
    screening by relevance (cannot occur at the site)
    frequency based screening (10-7/a for Paks NPP)
  Evaluation of the dependence among the hazards
    a table („matrix”) form – cross-correlation chart
    for all the possible hazard combinations, the possible relation type has to be identified and marked with a predefined symbol
    identification of hazard combinations including 3 or more hazards:
      mapping of root causes that may trigger such combinations
      studying the dependence in rows and columns of the cross-corr. chart

## Slide 9: Selection of Combined External Hazards – Possible relation types
↗↙ | one hazard is a prerequisite of the other hazard
↙↗ | one hazard may cause the other hazard, the impact mechanisms of the single hazards are similar or the same
↙↗ | one hazard may cause the other hazard, the impact mechanisms of the single hazards are different
 | correlated hazards, the impact mechanisms of the single hazards are similar or the same
 | correlated hazards, the impact mechanisms of the single hazards are different
 | independent hazards, the impact mechanisms of the single hazards are similar or the same
 | independent hazards, the impact mechanisms of the single hazards are different
 | mutually exclusive hazards

## Slide 10: Screening of Combined External Hazards
  666 hazard combinations were mapped, consisting of 2 hazards
  In general, the same screening criteria as for single hazards
  Relation between the impact mechanisms of the single hazards:
    similar or the same (e.g. wind & snow to structures):
      hazards affect the same SSCs amplifying one another’s effects
      resistance against the combined load has to be assessed
    different (e.g. wind & high temperature)
      hazards do not affect the same SSCs or not with the same mechanisms
  Hazard combination specific screening criteria:
    hazards are mutually exclusive
    definition of a single hazard covers the other single hazard
    the impact of the hazard combination is not more severe than the effect of the more powerful hazard

## Slide 11: Screening of Combined External Hazards
  Detailed screening of hazard combinations was performed considering the following hazard categories:
    hydrological hazards;
    man-made external hazards;
    riverine events endangering the water intake facility;
    hazards related to the relevant areas of geosciences;
    meteorological hazards.
  For the sake of traceability and transparency screening not on a case-by-case basis, but looking at hazards within a group and then hazards related to different categories

## Slide 12: Screened-in Combined External Hazards
  handling of dangerous substances in severe weather conditions
  multiple accidents in nearby industrial facilities due to a common initiator of natural origin
  earthquake occurring when the ambient temperature is extreme (independent hazards)
  storm: high wind, extreme precipitation and thunder
  snowstorm and accumulated snow and strong wind: extreme wind and snow
  extreme warm weather: extremely high air temperature and high Danube temperature
  extreme cold weather: extremely low air temperature and surface ice on the Danube (and icing and snow)
  (geoscience related hazards, e.g. earthquake and soil liquefaction)
  (possible combinations of single hydrological events)
  (external hazards endangering the blockage of water intake from the river Danube – combinations of single endangering events)

## Slide 13: Hazard Assessment – Man Made Hazards
  A large number of dedicated deterministic analyses to determine the effects of an accident during handling dangerous substances in severe weather conditions -> do not pose more significant impact on the NPP safety than in moderate conditions – screened out from further assessment
  Multiple accidents in nearby industrial facilities do not pose a significant challenge to the NPP safety due to
    the distance between the hazard sources and the NPP
    the direction of the sources relative to the NPP
    and the different types of effects of the various sources

## Slide 14: Hazard Assessment – Natural Hazards
  Snowstorm: relative frequency of strong winds during intensive snowfalls
  Full correlation was conservatively assumed between the extreme (return) values of instantaneous, daily and weekly air temperatures, and cooling water temperature
  Earthquake occurring when the ambient temperature is extreme (independent hazards – dedicated approach)
    occurrence frequency of event i [1/a]
    duration of event i [year]
    N duration (in a year) when both events may occur simultaneously [year]
  Storm; Accumulated snow and strong wind:
    collected site specific data
    joint distribution function – bivariate extreme value distribution
      logistic dependence model
      extreme value distribution functions of single hazards as marginal distributions

## Slide 16: Plant Response and Fragility Analysis
  Earthquake occurring when the ambient temperature is extreme:
    failure of the HVAC system induced by below design basis seismic events during moderately extreme air temperature
    the potential processes and the corresponding fragility curves
    plant is sufficiently protected against low air temperature
  Storm: LOOP induced by high wind or lightning and simultaneously extreme precipitation
    cooling water of diesel generators are discharged to the same canalization system that is used for rainwater discharge
    plant is sufficiently protected against such scenarios
  Extreme warm and cold weather – plant response is almost the same to these events as to single hazards, not assessed further

## Slide 17: Plant Response and Fragility Analysis
  Accumulated snow and strong wind:
    thorough review of the already available structural analyses -> the fragilities assessed for single hazards are bounding
      some combinations were already considered
      dominant structural components in the fragilities do not coincide
    new scenario: LOOP (with wind fragility) during heavy snowfall
  Snowstorm – conservative expert judgement
    the conditional blockage probability of the air intake system to the diesel generators in case of a heavy snowfall is 0.1 (if no operator action is assumed)

## Slide 18: Event Logic Modelling
  Earthquake occurring in extreme warm weather
    Identification of event sequences leading to core damage (seismic failures leading to loss of HVAC system)
    Single hazard fragility curves could be used in the assessment
    CCDP for extreme warm weather situations when HVAC is not available was estimated based on conservative expert judgement
    No detailed PSA model, spreadsheet application to determine cut set frequencies, overall CDF, perform sensitivity analysis
  Extreme wind and snow
    New events:
      wind induced loss of off-site power during extreme snowfall
      wind induced switchyard failures leading to LNPS during extreme snowfall
      loss of the diesel generators due to snowstorm (blockage of air intake systems)
    Scenarios:
      wind induced LOOP AND snow induced failure
      snow induced switchyard failures AND blockage of the air intake filters to the DGs
    Event tree for extreme snow was utilized, quantification similar to single hazards

## Slide 19: Findings
  Earthquake occurring in warm weather
    CDF 1.74·10-7 /a
    same failures in full power operation and in LPSD (constant risk)
    considerable uncertainties, hence regarded as an upper bound
    fans and heat exchangers of the HVAC system and the seismically unqualified relays and cabinets are the dominant risk contributions
  Extreme wind and snow
    CDF 2.06·10-8 /a
    Dominant event sequences:
      LOOP due to high wind and the blockage of the air intake system of the DGs
      wind induced failure of the switchyard, subsequent failure of plant operation in island mode and the blockage of the air intake system of the DGs
    limited scope of uncertainty assessment showed remarkable uncertainties
  Several safety enhancement measures were proposed

## Slide 20: Conclusions
  An assessment of combined external hazards for the Paks NPP has lately been completed.
  The relevant load combinations have been identified and characterized
  The adequacy of protection against hazard combinations has been justified.
  The residual risk due to beyond design basis load combinations has been quantified and the main risk contributors have been identified.
  The assessment followed the commonly exercised steps in this domain:
    hazard selection and screening,
    hazard assessment,
    evaluation of plant protection,
    plant response and fragility analysis,
    development of event sequence models for hazard initiated plant transients
    risk quantification and evaluation of results.
  The Paks NPP is sufficiently protected against the combined external hazards.

## Slide 21: Thank you for your attention!