## Slide 1: ÚJV Řež, a. s., Czech Republic PSA Applications for Dukovany NPP Stanislav Husťák

## Slide 2: Presentation Outline
Overview of Living PSA project for Dukovany NPP
Regulatory Decrees and guides for PSA applications
Performed PSA applications for Dukovany NPP
Main outputs
Main insights and conclusions

## Slide 3: PSA for Dukovany NPP
  Dukovany NPP
  VVER-440/213 type plant in the Czech Republic
  four almost identical units, 500 MWe each
Living PSA Project
  developed and maintained in ÚJV Řež, a. s., for Dukovany NPP
    RiskSpectrum® PSA software
  basis for PSA applications at Dukovany NPP
    evaluation of Technical Specifications (TS)
    selection of important components
    risk monitoring (the most extensive one, Safety Monitor™ is utilized)
    analysis of occurred events, analysis of modifications etc.
  the first two applications are subject of this presentation

## Slide 4: Living PSA Scope
Full-scope Level 1 & Level 2 PSA
  all plant operating modes
  internal initiating events (IEs), internal and external hazards,
  risk from reactor core as well as from spent fuel pool (SFP)
    Core Damage Frequency (CDF)
    Fuel Damage Frequency (FDF) = CDF + frequency of fuel damage in SFP
Fully integrated PSA model
  all plant operating states (POSs) and IEs are modeled in the same PSA project
    no separate PSAs for shutdown operation, hazards or SFP risk

## Slide 5: Regulatory Decrees and Guidelines
Czech implementing Decree 162/2017
  requires to use PSA applications for the selected purposes
  Czech regulatory safety guides
  support some PSA applications incl. those required by Decree
  BN-JB-2.5 (analogous to IAEA SSG-3)
    supports PSA applications generally
  BN-JB-2.6 (analogous to US NRC RG 1.174)
    supports RIDM for changes initiated by plant
  BN-JB-2.7 (analogous to US NRC RG 1.177)
    supports TS evaluation
  BN-JB-2.8 (analogous to NEI-00-04)
    supports PSA based selection of important components

## Slide 6: Evaluation of Technical Specifications
Implementing Decree 162/2017
  it requires to assess both the need for TS modifications and acceptability of TS changes initiated by plant
  Regulatory safety guide BN-JB-2.7
  supports TS changes initiated by plant as well as AOT adequacy
    incremental conditional core damage probability (ICCDP) ≤ 5 × 10‑7
    incremental cond. large early release probability (ICLERP) ≤ 5 × 10-8
    acceptable yearly risk increase is defined in BN-JB-2.6 (not applicable for evaluation of AOT adequacy since it is not related to change)
  guideline and discussion for comparison of alternatives
    when plant would choose this option to justify TS change
    approximately the same level of conservatism should be applied in models for compared alternatives

## Slide 7: Evaluation of Technical Specifications
TS evaluation performed recently for Dukovany NPP
  main objectives
    identification of the eventual need for TS modification
    identification of potential for AOT extension
    comparison of alternatives for the cases selected by plant
  scope of evaluation
    more than 250 cases for various combinations of limiting conditions for operation (LCOs) and AOTs
    diverse and mobile (DAM) requirements for availability were included
    risk associated with AOT in Mode 1 was assessed, several evaluations were done also for other Modes
    unit No. 1 was selected as a representative one
    internal and external hazards were included in calculation of AOT risk

## Slide 8: Evaluation of Technical Specifications
Main features
  entry into LCO selected for calculation
    identified most unfavorable case of entry into each LCO
    limited to single failure or single common cause failure (CCF)
    conditioning of CCF was applied when components redundant to failed one are not subsequently tested (if CCF is credited in PSA)
  calculation of risk associated with AOT
    such risk was compared with criteria for ICCDP and ICLERP
    determination of maximal AOT for given LCO, it allows plant to identify potential proper candidates for AOT extension
  RiskSpectrum PSA software was used for calculations

## Slide 9: Evaluation of Technical Specifications
Main outputs
  all evaluated LCOs have been found adequate
  a few exceptions were identified
    some cases of motor operated valve (MOV) unavailability when CCF conditioning was applicable
  TS modifications for Dukovany NPP were proposed
    mainly to decrease risk associated with AOT for several cases of MOV unavailability
    they include new TS requirements to test MOVs in the other redundant divisions when one of the redundant MOVs fails
    sensitivity analyses to show benefit of modifications were performed
  finally, plant made several changes in TS based on these proposals

## Slide 10: Evaluation of Technical Specifications
Comparison of alternatives
  the following alternatives were compared for selected cases
    risk from continuation at power with unavailable component
    vs. risk from shutdown after AOT expires
    for the same time period
  main insights
    continuation at power operation has not been found to be better option in the analyzed cases
    output of comparison is often highly dependent on expected time to repair, duration of transition states, etc.
    output of comparison was not often decidable, e.g. when output based on CCDP comparison gave results different from output based on CLERP comparison for the same component unavailability

## Slide 11: Comparison of Alternatives
continuation of operation in Mode 1; shutdown after AOT expires
Note: Risk from time interval corresponding to startup in shutdown case (just after repair is completed) is added at the beginning of calculation for both alternatives
Unavailability of essential service water (ESW) division
  CCDP and CLERP dependent on time to repair (TR) is shown

## Slide 12: Selection of Important Components
Regulatory Decree 162/2017
  requires to identify components with impact on plant safety using PSA for various purposes
  Regulatory safety guide BN-JB-2.8
  support for PSA based selection of important components
    regardless of the purpose (it is not specified here)
    importance measures are utilized to assess (non-negligible) impact
  important component
    FV (Fussell-Vesely) for sum of component failure modes ≥ 0.005
    the highest Risk Achievement Worth (RAW) ≥ 2 (including CCF)
    either in FDF calculation or in LERF calculation
    either for internal IEs (incl. internal hazards) or for external IEs

## Slide 13: Selection of Important Components
Performed for components at Dukovany NPP
  both for plant and for regulator
  PSA based using importance measures
  integrated PSA model was used
    importance measures were not determined separately for shutdown states nor for internal hazards
    List of important components based on PSA
  mostly safety or safety-related components
  some non-safety components
    added to plant list of „non-categorized equipment with impact“ for graded treatment

## Slide 14: Main Insights and Conclusion
Living PSA project for Dukovany NPP
  effective tool to control and reduce plant risk level
    in accordance with requirements of Regulatory Decree
    especially, PSA is used to propose measures at plant if necessary
    evaluation of TS adequacy to identify the need for TS changes contributes to this PSA objective as well
  provides support for risk informed decision making at Dukovany NPP
    for changes initiated by plant
    it includes also identification of potential for such kind of changes
  provides support for site inspectors of Czech regulator as well
    list of important components based on PSA importance measures is used as a support to determine significance of issues and findings

## Slide 15
Thank you for your attention