## Slide 1
Global Expertise • One Voice
Alvin Robertson – Fellow Engineer Westinghouse Electric Jim Lynde – Byron Operations Manager, PWROG PSC Chairman
PSAM16 06/27/2022
Operational Guidance to Improve Industry Benefit of Alternate Equipment and Strategies

## Slide 2: Risk Informed Procedures
The Pressurized Water Reactor Owners Group (PWROG) has recently championed several efforts to increase collaboration between nuclear power plant Probabilistic Risk Assessment (PRA) experts and Operation’s procedure writers.
The results of these efforts has allowed for nuclear power plants to risk inform plant procedures, improve modeling of operator actions in PRA, and ultimately reduce risk and promote the health and safety of the public.

## Slide 3: Flex Support Guidelines Additional Defense in Depth
A key insight from this collaboration was the need for, and development of, an industry framework for generating WRITTEN GUIDANCE to increase the benefit of alternate strategies.
As the industry expands the use of alternate equipment (installed and portable), standardization of terminology, application, and PRA modeling of flexible equipment operation is desired.
To that end, a new category of industry Guidelines has been defined: Flex Support Guidelines Additional Defense in Depth (FSG+DD).

## Slide 4: Maintain or Restore Function
FSG+DD strategies may be utilized to supplement current guidance used to maintain or restore a function when the plant is outside a Design Basis CREDITED MITIGATION STRATEGY.
Additionally, these strategies may be utilized within a plants Design Basis to compensate for equipment that is DEGRADED or out of service to maintain a function.

## Slide 5: Risk Informed Procedure Writers Guide
Standardized methodology for generating WRITTEN GUIDANCE that utilizes manual actions, installed systems and portable equipment such as FLEX to improve site operations and accident mitigation. These improvement areas could include, but are not limited to, the following:
  Providing additional defense in depth during Emergency Operations
  Online risk reduction
  Outage risk reduction
  Generation risk reduction
  Maintenance activity efficiency
  Maintaining SSC Availability
  Supporting a Notice of Enforcement Discretion (NOED)
  Supporting Significance Determination Process
  Supporting Risk Informed Completion Times (RICT)

## Slide 6: CREDITING MANUAL ACTIONS TO MAINTAIN SSC FUNCTION AVAILABLE
When an SSC must be rendered temporarily unavailable due to maintenance or testing, the SCC may be considered available by crediting FSG+DD (installed or portable) equipment to restore the SSC within the AVAILABLE TIME.
Actions to restore the PRA CREDITED FUNCTION within the AVAILABLE TIME
  ASSIGNED OPERATOR is Briefed, Designated or Dedicated such that the action can be accomplished
  ADEQUATE COMMUNICATION is established

## Slide 7: Implementing FSG+DD Guidance
FSG+DD guidance may be incorporated into existing plant documents including but not limited to:
  Emergency Operating Procedures (EOPs)
  Abnormal Operating Procedures (AOPs)
  Alarm response Procedures (ARPs)
  Normal Operating Procedures (NOPs)
FSG+DD guidance may be standalone if incorporating into existing documents is not practical.

## Slide 8: FSG+DD Impact on DBE Credited Mitigation Considerations
The design basis of the plant is governed by the Updated Final Safety Analysis Report (UFSAR) and Technical Specifications.
Implementation of an FSG+DD strategy should be evaluated to ensure that it does not prevent the successful operation of available installed plant equipment credited in the design basis.
Portable equipment should not be used to replace the available minimum installed equipment required by the plant Technical Specifications or the accident analysis chapter of the FSAR.
Potential impact on Time Critical and Time Sensitive actions should be evaluated prior to implementation of an FSG+DD strategy.

## Slide 9: FSG+DD Strategies Supporting Partial Loss of Function
FSG+DD guidance may be utilized to restore a partial loss of function, or in support of maintenance activities if the following conditions are met:
  The SSC (component, train, bus, channel) on which the FSG+DD guidance will be utilized is/will be inoperable AND unavailable
  Operable SSCs AND applicable implementation strategy credited for maintaining or restoring the partially lost function are unaffected by the FSG+DD guidance (i.e., opposite train equipment)

## Slide 10: FSG+DD Strategies Supporting Security Response
FSG+DD strategies can be utilized to optimize plant physical security.
Idaho National Laboratory (INL) report, “Integration of FLEX Equipment and Operator Actions in Plant Force-On-Force Models with Dynamic Risk Assessment” integrates commercial Force-on Force modelling tools with INLs FLEX deployment model.
The results demonstrate that, even in the extreme case of a successful adversarial attack, deployment of portable equipment can result in a significantly high likelihood of preventing radiological release.

## Slide 11: FSG+DD Strategies Supporting Fire Response
FSG+DD strategies may be utilized to restore a function lost due to a fire.
Fire response procedures and Pre-Plans may contain WRITTEN GUIDANCE to utilize FSG+DD strategies to replace equipment affected by the fire.

## Slide 12: FGS+DD Strategies for TS Allowed Outage Time (AOT) Extension and Shutdown Risk Reduction
FSG+DD strategies can be leveraged to enable online maintenance of installed equipment by incorporating into the plant PRA model and comparing the resulting risk-achievement-worth (RAW) to the risk acceptance guideline in the NRC regulation RG 1.177.
The resulting AOT extension may shift component maintenance from a refueling outage period to online maintenance which may reduce the burden of outage maintenance, allow more effective outage planning, and increase a Nuclear Power Plant’s capacity factor.

## Slide 13
Significant Benefits of Portable Equipment
Developing a Defense-in-Depth Strategy for EOP or AOP
  Mitigation of Design Basis Accidents or Beyond
  Mitigation of Fire, Flood, Tornado Event
Improving Security Bounding Time to Core Damage
Maintenance Window Support
  Alternate pump or power options during maintenance window
Outage Benefits during train outages
  Power for testing
  Reduction in Outage Critical Path by crediting for S/D Risk

## Slide 14
Examples of Defense in Depth for EOP or AOP
The following are actual examples of EOP or AOP changes resulting in significant (up to 50%) reduction in CDF
Alternate Aux FW pump for loss of heat sink events
Alternate battery power for Tornado damage
FLEX used to provide cooling for equipment used for accident mitigation including ECCS, ESW, and Aux FW pumps
Local alternate power to equipment deenergized from fire or flood event.

## Slide 15
Examples of Improving Security Bounding Time
The following are proposed examples credited operator actions that will improve security bounding time.
Portable equipment to power security equipment
  Detection
  Monitoring
  Local lighting
  Debris removal
Low Flow core injection for RCS inventory
Alternate recovery of function after hostile equipment damage
Provide cooling for equipment included for Security procedure

## Slide 16
Examples of Maintenance Window Support
The following are proposed and actual examples of use of portable equipment during on line maintenance window
Flushing of underground piping after a cleaning maintenance.
Provide pump capacity during intense precipitation event that would have resulted NPDES violation of overflowing plant flume
FLEX supplied 480V power to service buildings during power line maintenance
Alternate Circ Water Make/up to support normal maintenance

## Slide 17
Examples of Outage Benefits
The following are proposed or actual examples of use of portable equipment during outage
Contingency Aux FW credited to improve shutdown risk
Contingency power to Loop Stop Isolation valves reduce critical path and allow loop isolation at higher decay heat level
Spent fuel pool cooling or spray as back up or supplement to normal cooling to improve time to boil calculations
Bus outage support for lighting, rad monitors, indication, valve stroke, etc. This actual example resulted several hours of critical path reduction.

## Slide 18
The potential for planned and unplanned use of portable equipment and local operator actions is significant and industry collaboration will foster innovation.
The benefits of portable equipment and local operation will provide an incentive for utilities to invest in procedure development and potential additional portable equipment.
Risk Informed Tech Spec completion times may included defense in depth Risk Management Actions which may prevent a T.S. shutdown or provide options to move traditional outage work to on line work.
Conclusion

## Slide 19: Conclusion
The industries considerable investment in FLEX assets are currently underutilized.
The PWROG has developed a standardized methodology for generating WRITTEN GUIDANCE that utilizes manual actions and FSG+DD strategies to improve site operations and accident mitigation.
This guidance will be available to the industry via a Risk Informed Procedure Writers Guide.

## Slide 20
Questions?