## Slide 1
A Model-Based Framework for Built-in Automatic Periodic Surveillance Testing in Plant Protection Systems
2026.07.22
Tae Young Jhee, Tae Ryoun Kim, Soonae Lee, Jonghyun Kim*
M.S. Student, Department of Nuclear and Quantum Engineering Korea Advanced Institute of Science and Technology (KAIST), Republic of Korea
Nuclear I&C and Autonomous Operation Lab
Notes: Good afternoon, everyone.
My name is Tae Young Jhee. I am a master's student in the Department of Nuclear and Quantum Engineering at KAIST. Today, I will present a model-based framework for built-in automatic periodic surveillance testing in plant protection systems.

## Slide 2
Contents
Introduction
Method
3. Results
4. Conclusion
5. Future Work
Notes: Here is the Content outline.
First, I will explain why surveillance testing of the plant protection system needs further automation. Then I will introduce our built-in automatic testing method, its implementation as a state-transition model, and the simulation results. I will finish with conclusions and future work.

## Slide 3
Introduction

## Slide 4
1. Introduction
Background
Plant Protection System (PPS)
Continuously monitors safety-critical plant variables
Generates a trip when a variable exceeds its setpoint
Redundant, independent channels with majority voting
(e.g., 2-out-of-4) to avoid spurious trips
Performs reactor trip and ESF actuation
Periodic Testing of the PPS
Required by plant Technical Specifications (IEEE 338 / RG 1.22)
Test interval (~31 days) — one channel at a time: channel bypassed, tested, and returned to service
Functional tests — performed manually by operators according to procedures
Fig. Plant Protection System
Notes: The plant protection system, or PPS, is a key safety system in a nuclear power plant. It continuously monitors safety-related process variables. When a variable exceeds its trip setpoint, the bistable logic generates a channel-level trip signal.
As shown in the figure, the PPS consists of four redundant and independent channels. The coincidence logic applies two-out-of-four voting to the channel trip signals, so that a single spurious signal does not initiate actuation. The voted result initiates a reactor trip or engineered safety features actuation.
Because the PPS performs safety functions, plant Technical Specifications require periodic surveillance testing. IEEE Standard 338 defines the surveillance-testing criteria, while Regulatory Guide 1.22 provides guidance on periodic testing of protection-system actuation functions.
A typical surveillance interval is about 31 days. One channel at a time is bypassed, tested, and returned to service. In conventional plants, these functional tests are generally performed manually by operators following approved procedures.

## Slide 5
1. Introduction
Background
PPS Periodic Testing Problem
Labor- and time-intensive
- Each channel is tested manually, requiring significant time and staffing
Human error during testing
- Test and restoration errors can cause inadvertent trips or latent unavailability (NUREG/CR-5775)
Undetected failures between tests
- A fault remains latent until the next surveillance test
- Average unavailability grows with the test interval (NUREG/CR-5775)
- Test frequency is limited by the manual testing burden (Tech. Spec. intervals ≈ 1 month)
Fig. Average system availability for short and long surveillance test intervals
Notes: So, what is the problem with manual periodic testing?
First, it is labor- and time-intensive. Every channel is tested manually, which takes significant time and staffing.
Second, human error during testing. As reported in NUREG/CR-5775, test and restoration errors can cause inadvertent reactor trips, or leave a channel unavailable without anyone noticing.
Third, failures between tests remain undetected. A fault stays latent until the next surveillance test, so the average unavailability grows with the test interval. The figure shows this clearly: with a short interval, on the left, average availability stays high; with a long interval, on the right, it degrades.
Ideally, we would simply test more often. However, the burden of manual testing limits its practical frequency to about once a month, highlighting the need for automation.

## Slide 6
1. Introduction
Current Plant Protection System Testing Practice
Most surveillance tests in conventional NPPs require direct or indirect operator intervention
Incomplete automation requiring operator involvement (manual tests, manually-initiated automatic tests)
Variable-setpoint bistable and actuation-level tests remain manual
Table. Plant Protection System Test Methods
Test Scope |  | Large-Scale NPPs | 
 |  | Common Q / AC160 | POSAFE-Q PPS
Bistable Logic Functional Test | Fixed Setpoint | Self-Diagnostics and Normal Testing | Manually Initiated Automatic Logic Test
 | Variable Setpoint | Manual Test | Manual Test
Coincidence and Actuation Logic Functional Test | Coincidence Logic | Self-Diagnostics and Normal Testing | Manually Initiated Automatic Logic Test (Sequential testing through the RPS initiation-circuit contacts)
 | Actuation Logic | Manual Test | 
Actuation Circuit and Manual Trip Functional Test | Actuation Circuit | Manual Test (RT+ESFAS) | Manual Test (RT)
 | Manual Trip | Manual Test (RT+ESFAS) | Manual Test (RT+ESFAS)
Notes: Some degree of test automation already exists. This table compares the test methods of two representative digital PPS platforms used in large-scale nuclear power plants: Common Q, based on AC160, and POSAFE-Q.
The blue entries indicate tests supported by built-in automation, such as self-diagnostics, normal testing, and automatic logic testing. However, the current level of automation remains limited. In POSAFE-Q, automatic logic tests must still be initiated by an operator. In both platforms, variable-setpoint bistable tests and actuation-level tests remain manual.
Therefore, most surveillance tests still require direct or indirect operator intervention, highlighting the need for more comprehensive automation.

## Slide 7
1. Introduction
FPGA-Based Protection System Testing
From PLC-Based to FPGA-Based Protection Systems
Conventional PLC-based systems: limitations in reliability, cybersecurity, and supportability
Adoption of FPGA-based protection system design in next-generation NPPs
- Parallel, deterministic hardware execution without an operating system on the FPGA logic fabric (Table)
- New failure modes from platform transition; heterogeneous architectures increase testing complexity • Test logic can be built into the FPGA, running in parallel with protection logic ▶ Need for a new testing framework reflecting FPGA characteristics
Table. Comparison of FPGA/PLC-Based Protection System Characteristics
Notes: At the same time, the underlying platform technology is evolving. Nuclear safety I&C systems are increasingly adopting FPGA-based designs as an alternative to conventional PLC-based platforms, motivated by reliability, cybersecurity, and long-term supportability.
As summarized in the table, the FPGA logic fabric executes functions directly in hardware, enabling parallel and deterministic operation without relying on an operating system, interrupts, or context switching.
From a testing perspective, this transition presents both challenges and opportunities. New failure modes and heterogeneous architectures increase testing complexity. At the same time, test logic can be embedded in the FPGA and executed concurrently with the protection logic.
Together, these factors motivate a new testing framework designed specifically for FPGA-based protection systems.

## Slide 8
1. Introduction
Testing Framework for the FPGA-Based PPS
PPS testing was analyzed in terms of test automation, test methods, and regulatory requirements
- Test categories: Normal Testing, Automatic/Manual Periodic Testing, and Self-Diagnostics
 | Normal Testing | Automatic Periodic Testing | Manual Periodic Testing | Self-Diagnostics
Purpose | Online monitoring of signal and logic status | Automated verification of protection logic functions During Operation | System Integrity Verification During Reactor Shutdown | Monitoring of Hardware Failures and Communication Faults During Operation
Test Method | Passive monitoring and consistency checks | Generate and inject test signals to verify expected system outputs and normal operation | Operator-performed surveillance testing | Detect hardware failures, communication faults, and data errors in real-time
Test Scope | Signal validation, setpoint validation, logic-output validation | Bistable logic, coincidence logic, actuation logic | Actuation circuit, manual trip, manual actuation functions | System status, communication integrity, and I/O diagnostics
Notes: We analyzed PPS testing in terms of test automation level, test method, and regulatory requirements. Based on this analysis, we classified PPS testing into four categories.
Normal testing uses passive consistency checks to monitor input signals, setpoints, and logic outputs during operation. Automatic periodic testing actively generates and injects test signals to verify the correct response of bistable, coincidence, and actuation logic without interrupting plant operation.
Manual periodic testing is performed by operators, during reactor shutdown, to verify downstream functions such as actuation circuits, manual trips, and manual actuation. Self-diagnostics continuously detects internal hardware, communication, data, and I/O faults during operation.
This study focuses on automatic periodic testing of protection logic.

## Slide 9
1. Introduction
Need for Automatic Periodic Testing
Normal Testing
Limited capability to verify the functional integrity of the protection logic
- Verifies only normal (non-trip) outputs with process variables
- Trip determination logic remains unverified (restricted abnormal signal injection)
Self-Diagnostics
Detects hardware/communication faults (No protection logic integrity verification)
Need for Automatic Periodic Testing
Online verification: injects abnormal test signals to verify actual operation of trip logic and output paths
Automated execution: performed at predefined intervals without operator intervention
Ensured test coverage: functional verification of the protection logic and output paths
Notes: Why do we focus on automatic periodic testing? Because normal testing and self-diagnostics cannot fully verify the trip function.
Normal testing checks signals and logic outputs based on actual process variables. During normal operation, these variables remain within the non-trip range, so normal testing can verify only the non-trip response shown in blue. Because it does not apply abnormal test inputs, the trip response, as shown in the table.
Self-diagnostics detects hardware and communication faults, but it does not verify the functional integrity of the protection logic.
Automatic periodic testing closes this gap. It injects controlled test signals representing abnormal conditions during operation and checks whether the trip logic and output paths produce the expected response. The test is performed at predefined intervals without operator intervention, providing online functional test coverage of the protection logic and output paths.

## Slide 10
1. Introduction
Research Objective
Development of an Automatic Periodic Testing Method for the Plant Protection System
Procedure-based manual tests
Manually-initiated automatic tests
Incomplete automation requiring operator intervention
Research Process
1
Define Automatic Periodic Testing Methods
2
Define Test Procedures
3
Model Test Procedures using State Transition Models
4
Implement the Model via MATLAB Stateflow
Proposed a Built-in Automatic Periodic Testing Method
Developed an HDL-compatible Stateflow model
Model-level simulation and pre-RTL clock-level behavior
Limitations of Existing Research
Research Results
Notes: Based on this need, the objective of this study is to develop an automatic periodic testing method for the PPS.
The left side summarizes the limitations of existing approaches: procedure-based manual testing and manually initiated automatic testing, both of which still require operator intervention.
The center shows our four-step research process. First, we defined the automatic periodic testing method. Second, we specified the test procedures. Third, we represented these procedures as state-transition models. Finally, we implemented the models in MATLAB Stateflow.
The right side summarizes the results. We proposed a built-in automatic periodic testing method, developed an HDL-compatible Stateflow model, and demonstrated its behavior through model-level and pre-RTL clock-level simulations.

## Slide 11
2. Method
Notes: [Slide 11 | ~0:05 | 누적 8:00]
Now, the method.

## Slide 12
2. Method
Automatic Periodic Testing
Test Signal Identification and Isolation
Tag test signals to distinguish them from actual process signals
Prevent propagation into the actual signal path
(Functional Isolation)
Prevent any impact on the safety functions of the protection system
Verify system integrity via test input injection during online operation
Generate and inject test inputs within the controller per test cycle
Compare the observed protection-logic output with the expected trip output
Monitor test results via the MTP (Maintenance and Test Panel)
Fig. Concept of Built-in Automatic Testing
Notes: The core concept is built-in automatic testing with functional isolation. The figure on the right illustrates this concept.
The test logic is implemented within the same FPGA-based processor as the protection logic. During each test cycle, it generates a test input representing an abnormal condition, such as a value above the trip setpoint, and applies it to the protection logic.
For safe online testing, each test signal carries a test identifier that distinguishes it from actual process signals. Any output carrying this identifier is routed only to the test logic and blocked from the actual protection signal path. This provides functional isolation between the test function and the safety function.
The test logic compares the observed protection-logic output with the expected trip output and sends the result to the Maintenance and Test Panel, or MTP.
This method enables automatic online functional verification of the protection logic while maintaining isolation from the safety function.

## Slide 13
2. Method
Automatic Periodic Test Implementation and Development Procedures
① Define States and Transition Conditions
• Derive the states and transitions of the automatic PST sequence
• Represent the test procedure as a state-transition model
② Stateflow Test-Logic Modeling and Simulation
③ Protection-Logic Integration and FSM Transition
• Build an HDL-compatible model of the linked test/protection logic
④ FPGA Clock-Level Timing and VHDL Generation
• Generate VHDL code using MATLAB HDL Coder
⑤ Preliminary HDL Verification
• Verify the generated HDL using MATLAB HDL Verifier
Notes: We implemented the proposed method in five steps.
First, we defined the states and transition conditions of the automatic test sequence and represented the test procedure as a state-transition model. Second, we modeled and simulated the test logic in MATLAB Stateflow. Third, we integrated the test logic with the protection logic to develop an HDL-compatible finite-state-machine model.
Fourth, we simulated the clock-cycle-level timing and generated VHDL code using MATLAB HDL Coder. Finally, we performed preliminary verification of the generated HDL using MATLAB HDL Verifier.

## Slide 14
3. Results
Notes: [Slide 14 | ~0:05 | 누적 10:15]
First, the model-level results.

## Slide 15
3. Results
Stateflow Model-Level Simulation
The Stateflow model generated a tagged test input and captured the simulated trip response
The captured response was compared with the expected trip to generate a pass/fail result
Two PST cycles were executed; the downstream actuation signal remained inactive in the simulation
Fig. Model-level timing of the Stateflow automatic PST sequence
Notes: This timing diagram shows the key interface signals of the Stateflow model over two automatic PST cycles.
Periodic Test Enable remains asserted throughout the simulation. At the beginning of each cycle, Test Active is asserted, indicating that the automatic test sequence is in progress.
During this interval, Test Stimulus Valid is asserted for each injected test input, and Test Result Valid is asserted when the corresponding result becomes available. The captured response is then compared with the expected trip output to determine the pass-or-fail result.
After all test cases are completed, Test Active is deasserted and Test Complete is asserted. The model then remains in standby until the next test cycle.
Most importantly, Propagation to Downstream Logic remains deasserted throughout both cycles, confirming functional isolation.
Overall, the results show that the automatic PST sequence operates as designed at the model level.

## Slide 16
3. Results
Pre-RTL FPGA Clock-Level Timing Simulation
The test and protection logic were linked in an HDL-compatible MATLAB model; VHDL code was generated before RTL synthesis
A test input at clk 3 produced the protection-logic output at clk 6, corresponding to a 3-cycle delay
The test output was captured at clk 7 and the test result was generated at clk 11
Fig. Pre-RTL FPGA clock-level timing of linked test and protection logic
Notes: Next, we linked the test and protection logic in an HDL-compatible model and performed a pre-RTL clock-cycle simulation. Here, one simulation tick represents one FPGA clock cycle.
As shown in the figure, at clock 3, Test Stimulus Valid is asserted, and Test Stimulus Value is applied to Bistable Logic Input. The response propagates through Bistable Trip Register and Trip Logic Input Register, and Bistable Logic Trip Output is asserted at clock 6. This corresponds to a three-cycle logic-path delay.
At clock 7, Trip Output Capture is asserted, indicating that the response has been captured. Test Result Valid is then asserted at clock 11 after the pass-or-fail comparison.
VHDL code was generated from this model, providing the basis for subsequent RTL verification and FPGA implementation.

## Slide 17
4. Conclusion
Notes: [Slide 17 | ~0:05 | 누적 12:30]
Let me summarize.

## Slide 18
4. Conclusion
PROPOSED METHOD
• The built-in PST design incorporates test-signal identification and functional isolation
• System integrity is verified through test-input injection during online operation
MODEL IMPLEMENTATION AND SIMULATION RESULTS
• The automatic PST sequence was developed as a Stateflow test-logic model
• Test-input generation, trip comparison, and result reporting were simulated at the logic-model level
• Linked test/protection-logic timing was simulated at the FPGA clock-cycle level
• VHDL code was generated from the model before RTL synthesis
Notes: In summary, this study makes two main contributions.
First, we proposed a built-in automatic PST design based on test-signal identification and functional isolation. This design enables online verification of the protection logic through test-input injection while preventing test signals from propagating into the actual protection signal path.
Second, we implemented the automatic PST sequence as a Stateflow test-logic model. Test-input generation, trip-response comparison, and result reporting were simulated at the model level. The linked test and protection logic were then simulated at the FPGA clock-cycle level, and VHDL code was generated for subsequent RTL verification and synthesis.
Overall, these results demonstrate the model-level feasibility of built-in automatic PST for FPGA-based protection systems.

## Slide 19
5. Future Work

## Slide 20
5. Future Work
PROGRESSIVE VERIFICATION | Stateflow model > Generated HDL > Target FPGA hardware
FUNCTIONAL & ROBUSTNESS V&V
• Run requirement-based and fault-injection tests
• Assess measurement uncertainty, signal noise, and communication delays; define tolerance, timeout, and retry criteria
QUANTITATIVE BENEFIT
• Establish baselines from current manual PST procedures
• Quantify expected reductions in test duration and operator involvement
• Quantify reductions in Average system unavailability
HDL-TO-FPGA IMPLEMENTATION
• RTL synthesis and ModelSim testbench generation
• Verify Stateflow model–FPGA code equivalence via co-simulation and code coverage
Notes: This study addresses framework- and model-level feasibility. Future work is organized into three areas.
First, HDL-to-FPGA implementation. We will perform RTL synthesis and develop ModelSim testbenches. We will then verify functional equivalence between the Stateflow model and the generated HDL through co-simulation and assess code coverage.
Second, functional and robustness V&V. We will conduct requirements-based and fault-injection tests under measurement uncertainty, signal noise, and communication delays. These results will be used to define tolerances, timeouts, and retry criteria.
Third, quantitative benefit assessment. We will establish baselines from current manual PST procedures and quantify expected reductions in test duration, operator involvement, and average system unavailability. These metrics will support risk-informed assessment.
Verification will progress from the Stateflow model to the generated HDL and finally to the target FPGA hardware.

## Slide 21
Thank you for listening
Notes: [Slide 21 | ~0:20 | 누적 15:05]
That concludes my presentation. Thank you very much for your attention. I would be happy to take any questions.

## Slide 22
References
[1] i-SMR Technology Development Project Agency, Innovative Small Modular Reactor (i-SMR) Catalog, 2023.
[2] KHNP, “Periodic Surveillance Testing Improvement for Digital Plant Protection System (AC160 Platform),” 2009.
[3] U.S. NRC, Regulatory Guide 1.118, Rev. 3, Periodic Testing of Electric Power and Protection Systems, 1995.
[4] U.S. NRC, Regulatory Guide 1.22, Periodic Testing of Protection System Actuation Functions, 1972.
[5] IEEE, IEEE Std 338-2022, Criteria for the Periodic Surveillance Testing of Nuclear Power Generating Station Safety Systems, 2023.
[6] U.S. NRC, Regulatory Guide 1.152, Rev. 3, Criteria for Use of Computers in Safety Systems of Nuclear Power Plants, 2011.
[7] IEC, IEC 60671:2007, Nuclear Power Plants — Instrumentation and Control Systems Important to Safety — Surveillance Testing, 2007.
[8] U.S. NRC, NUREG/CR-7006, Review Guidelines for Field-Programmable Gate Arrays in Nuclear Power Plant Safety Systems, 2010.
[9] P. McNelles et al., “Failure Mode Taxonomy for Assessing the Reliability of Field-Programmable Gate Array-Based I&C Systems,” Annals of Nuclear Energy, vol. 108, pp. 198–228, 2017.
[10] C. Park and J. Ha, Probabilistic Safety Assessment, Brain Korea, 2003.
[11] U.S. NRC, NUREG/CR-5750, Rates of Initiating Events at U.S. Nuclear Power Plants: 1987–1995, 1999.
[12] U.S. Department of Defense, MIL-HDBK-217F-N2, Reliability Prediction of Electronic Equipment, 1995.
[13] D.-Y. Lee, J.-G. Choi, and J. Lyou, “A Safety Assessment Methodology for a Digital Reactor Protection System,” International Journal of Control, Automation, and Systems, vol. 4, no. 1, pp. 105–112, 2006.
[14] K. Lee, Development of an Automated Testing Method for Plant Protection System of Small Modular Reactor, KAIST, 2026.
[15] H.-T. Lim, “Development of an Innovative Reactor-Safety System for Multi-Module Small Modular Reactors,” Korean Nuclear Society Spring Meeting, 2026.
Notes: [Slide 22 | 발표 시 생략 — Q&A 대비용 참고문헌]