## Slide 1: A Bayesian Framework for Estimating Natural Hazard Impacts on Transmission Assets
Federico Sartore, Blazhe Gjorgiev, Giovanni Sansavini
Reliability and Risk Engineering Lab, ETH Zurich, Switzerland

## Slide 2
Motivation
Method
Results
Conclusion
Natural Hazards Impacts on Transmission Assets

## Slide 3
Motivation
Method
Results
Conclusion
Natural Hazards Impacts on Transmission Assets
a) Snow & Windstorms
b & c) Windstorms
d) Lightning
e & f) Flooding
Landslides, avalanches ...
Karagiannakis, G., Panteli, M., & Argyroudis, S. (2023). Fragility modeling of power grid infrastructure for addressing climate change risks and adaptation. Reliability Engineering & System Safety, 235, 109198
European Network of Transmission System Operators for Electricity (ENTSO-E). (2025). HVAC Nordic and Baltic Grid Disturbance Statistics 2024. Brussels: ENTSO-E.
b & c) Windstorms
d) Lightning

## Slide 4
Motivation
Method
Results
Conclusion
Natural Hazards Impacts on Transmission Assets
Challenges
Uncertainty
Coarse and incomplete data [1]
Highly specific, non-transferable studies [2]
Research question
What happened?
TERNA (2024). Quality of the transmission service
Xue, J., Mohammadi, F., Li, X., Sahraei-Ardakani, M., Ou. (2023). Impact of transmission tower-line interaction to the bulk power system during hurricane. Reliability Engineering & System Safety, 233, 109134.
Literature
Fragility curves
Is it possible to develop a data-driven framework that incorporates hazard-specific knowledge and captures the uncertainty of natural hazard events?

## Slide 5
Motivation
Method
Results
Conclusion
Natural Hazards Impacts on Transmission Assets
Challenges
Uncertainty
Coarse and incomplete data [1]
Highly specific, non-transferable studies [2]
Research question
What happened?
TERNA (2024). Quality of the transmission service
Xue, J., Mohammadi, F., Li, X., Sahraei-Ardakani, M., Ou. (2023). Impact of transmission tower-line interaction to the bulk power system during hurricane. Reliability Engineering & System Safety, 233, 109134.
Literature
Fragility curves
Is it possible to develop a data-driven framework that incorporates hazard-specific knowledge and captures the uncertainty of natural hazard events?
Finite element-based model [1]
Data-driven [2]
Dikshit, S., & Alipour, A. (2021). A moment-matching method for fragility analysis of transmission towers under straight line winds. Engineering Structures, 248, 113236.
Solheim ØR, et al. “Vaffel – a tool for forecasting transmission line failures based on Bayesian updating, reanalysis data and medium-range weather forecasts,” IEEE Acess, 2024

## Slide 6
Motivation
Method
Results
Conclusion
Bayesian Approach for Physically Informed Data-Driven Fragility Curves
Prior
Evidence
Posterior

## Slide 7
Motivation
Method
Results
Conclusion
Bayesian Approach for Physically Informed Data-Driven Fragility Curves
From finite element-based modeling [1]
Physically-informed prior
Conductor-conductor flashover
Prior Manipulation
Evidence
Posterior
Failure Dataset
1. Mazaheri, & Alipour. Department of Civil, Structural, and Environmental Engineering at Iowa State University
Prior

## Slide 8
Motivation
Method
Results
Conclusion
Bayesian Approach for Physically Informed Data-Driven Fragility Curves
Prior
Evidence
Posterior

## Slide 9
Motivation
Method
Results
Conclusion
Bayesian Approach for Physically Informed Data-Driven Fragility Curves
From a finite element-based [1]
Physically-informed prior
Prior
Conductor-conductor flashover
Dataset
9
Posterior
Exposure map
From data
Failure data (TERNA)
Weather data (COPERNICUS)
Evidence

## Slide 10
Motivation
Method
Results
Conclusion
Bayesian Approach for Physically Informed Data-Driven Fragility Curves
Prior
Evidence
Posterior

## Slide 11
Motivation
Method
Results
Conclusion
Bayesian Approach for Physically Informed Data-Driven Fragility Curves
Markov Chain Monte Carlo
Evidence
Prior

## Slide 12
Motivation
Method
Results
Conclusion
Bayesian Approach for Physically Informed Data-Driven Fragility Curves
Markov Chain Monte Carlo
Evidence
Prior

## Slide 13
Motivation
Method
Results
Conclusion
Wind gust
Results
Prior (5-50-95%) | Target (5-50-95%) | Posterior (5-50-95%)
0.0/0.0/0.8 | 15.6/20.3/26.1 | 13.2/17.5/22.5
Prior (5-50-95%) | Target (5-50-95%) | Posterior (5-50-95%)
126.2/582.0/1714.3 | 15.6/20.3/26.1 | 14.5/19.5/24.6
Wind average

## Slide 14
Motivation
Method
Results
Conclusion
Short-term weather forecast
Short-term: Assets likely to fail (Early warning)
Long-term:
Contingency generation
Grid analyses:
Resilience assessment
Grid analyses:
Vulnerability assessment
Climate projections
Model Deployment

## Slide 15: Conclusion
Motivation
Method
Results
Conclusion
Fragility curves can over/under estimate the failure risk.
Bayesian methods can regularize fragility curves calibration.
Fragility curves can capture uncertainty in natural hazards events.

## Slide 16: Thank you for your attention!
Federico Sartore
fsartore@ethz.ch
Linkedln

## Slide 17
Motivation
Method
Results
Conclusion
Bayesian Approach
Wind gust
MLE Approach
Results

## Slide 18
Motivation
Method
Results
Conclusion
Natural Hazards Impacts on Transmission Assets
Fragility Curves
Power Transmission
Finite element-based models [1]
Data-driven studies [2]
Limited research
1. Dikshit, S., & Alipour, A. (2021). A moment-matching method for fragility analysis of transmission towers under straight line winds. Engineering Structures, 248, 113236.
2. Solheim ØR, et al. “Vaffel – a tool for forecasting transmission line failures based on Bayesian updating, reanalysis data and medium-range weather forecasts,” IEEE Acess, 2024.

## Slide 19
Motivation
Method
Results
Conclusion
Wind gust
Wind average
Results
Prior (5-50-95%) | Target (5-50-95%) | Posterior (5-50-95%)
0.0/0.0/0.8 | 15.6/20.3/26.1 | 13.2/17.5/22.5
Prior (5-50-95%) | Target (5-50-95%) | Posterior (5-50-95%)
126.2/582.0/1714.3 | 15.6/20.3/26.1 | 14.5/19.5.5/24.6