## Slide 1
Probabilistic Safety Assessment and Management (PSAM 18)
A Dynamic Bayesian Network Approach for Modeling
High-Wind Probabilistic Safety Assessment in Nuclear Power Plants
Chaeyeon Go¹, Shinyoung Kwag¹*, Seunghyun Eem², Changuk Mun³, Daegi Hahm³
¹ Hanbat National University ² Kyungpook National University ³ Korea Atomic Energy Research Institute
Ph.D. Student
Civil Engineering

## Slide 2
Table of
CONTENTS
1
Introduction
Research Introduction · Research Background
2
Methodology
Proposed intensity-based DBN · Study Area and High Wind Scenarios
3
Case Studies & Extension
Case 1 · Case 2 · Extension to Real-Time Monitoring
4
Conclusion
Conclusion & Future work
2

## Slide 3
1 · INTRODUCTION
Research Introduction
After the 2011 Fukushima accident, external hazards became a serious concern for NPP safety.
Especially, regulators including the USNRC expanded external-hazard PSA to cover earthquakes, flooding, and high winds.
Among these external hazards, high winds act across the entire site, causing simultaneous SSC(Structures, Systems, and Components) damage and cascading failures.
Typhoons, Tornadoes, etc.
SSCs considered in this study
Auxiliary Building (AUX)
Emergency Diesel Generator Building (EDGB)
Essential Service Water (ESW) Intake Structure
Component Cooling Water (CCW) Heat Exchanger Building
Turbine Building (TB)
Switchyard Structure (SWY)
Figure 1. Fukushima NPP after the 2011 accident
3

## Slide 4
1 · INTRODUCTION
Research Background
To assess these hazards, NPPs have traditionally used ET–FT models.
However, ET–FT computes the damage probability independently at each wind speed, so it cannot capture how damage accumulates as wind speed rises.
Bayesian network (BNs) offer an alternative: they can represent complex inter-SSC dependencies, probabilistic inference, and uncertainty propagation.
But a static BN fixes the system state at a single point in time, so it cannot capture how damage states evolve as wind speed changes. A static BN gives only the conditional core damage probability (CCDP) at one wind speed. Core damage frequency (CDF = Σ CCDPᵢ·ΔHᵢ) requires CCDP across the whole intensity range. A static BN therefore cannot produce CDF.
Against this background, this study proposes an intensity-based dynamic BN (DBN) that uses wind intensity as the state-transition axis to model the integrated propagation and dependencies of SSC damage states.
4

## Slide 5
2 · METHODOLOGY
Proposed Intensity-based DBN
A static BN captures the system at only a single wind speed. It can only calculate the CCDP.
CDF needs CCDP over the whole intensity range. A static BN cannot produce CDF.
Traditional static Bayesian Network (BN)
C₁
Sys₁
C₂
+
C₃
Sys₂
C₄
+
C₁
Sys₁
C₂
+
CCDP
Seq2
+
·
Seq1
C₃
C₄
C₁
Sys₂
Sys₁
NSys₁
Seq2
CCDP
C₂
Seq1
ET-FT
One-top FT
Static BN
Sys₁
+
Sys₂
+
Sys₁
Sys₂
Seq₁
Seq₂
Seq₃
CD
CD
OK
Con-
sequence
Seq #
C₁
C₂
C₃
C₄
5

## Slide 6
2 · METHODOLOGY
Proposed Intensity-based DBN
A DBN links intensity slices with inter-slice edges. A state at one slice conditions the next. This models the transition and propagation of damage states.
Proposed Dynamic BN (DBN)
Figure 2. Intensity-based DBN
Fragility info.
Hazard info.
C₃
C₄
C₁
Sys₂
Sys₁
NSys₁
Seq2
CCDP
C₂
Seq1
dH
dCDF
Fragility based-
CPTs (conditional probability tables)
n=3 | C₁
Fail | 
Safe | 
n=2 | C₁
Fail | 
Safe | 
n=1 | C₁
Fail | 
Safe | 
Hazard curve Info.
Intensity
AEP
= 1
= 2
= 3
(Annual Exceedance Probability)
6

## Slide 7
2 · METHODOLOGY
Proposed Intensity-based DBN
Figure 3. Unrolled Intensity-based DBN
3
…
n
2
1
C₃
C₄
Sys₂
Sys₁
NSys₁
Seq2
CCDP
C₂
Seq1
dH
dCDF1
C₃
C₄
Sys₂
Sys₁
NSys₁
Seq2
CCDP
C₂
Seq1
dH
dCDF2
C₃
C₄
C₁
Sys₂
Sys₁
NSys₁
Seq2
CCDP
C₂
Seq1
dH
dCDFn
C₃
C₄
Sys₂
Sys₁
NSys₁
Seq2
CCDP
C₂
Seq1
dH
dCDF3
n=1 | C₁
Fail | -
Safe | -
CPT(N = 1)
C₁
C₁
C₁
7

## Slide 8
2 · METHODOLOGY
Proposed Intensity-based DBN
Figure 3. Unrolled Intensity-based DBN
3
…
n
2
1
C₃
C₄
Sys₂
Sys₁
NSys₁
Seq2
CCDP
C₂
Seq1
dH
dCDF1
C₃
C₄
Sys₂
Sys₁
NSys₁
Seq2
CCDP
C₂
Seq1
dH
dCDF2
C₃
C₄
C₁
Sys₂
Sys₁
NSys₁
Seq2
CCDP
C₂
Seq1
dH
dCDFn
C₃
C₄
Sys₂
Sys₁
NSys₁
Seq2
CCDP
C₂
Seq1
dH
dCDF3
n=2 | C₁ | 
 | Fail | Safe
Fail | - | -
Safe | - | -
CPT(N = 2)
C₁
C₁
C₁
8

## Slide 9
2 · METHODOLOGY
Proposed Intensity-based DBN
Figure 3. Unrolled Intensity-based DBN
3
…
n
2
1
C₃
C₄
Sys₂
Sys₁
NSys₁
Seq2
CCDP
C₂
Seq1
dH
dCDF1
C₃
C₄
Sys₂
Sys₁
NSys₁
Seq2
CCDP
C₂
Seq1
dH
dCDF2
C₃
C₄
C₁
Sys₂
Sys₁
NSys₁
Seq2
CCDP
C₂
Seq1
dH
dCDFn
C₃
C₄
Sys₂
Sys₁
NSys₁
Seq2
CCDP
C₂
Seq1
dH
dCDF3
n=3 | C₁ |  |  | 
 | Fail |  | Safe | 
 | Fail | Safe | Fail | Safe
Fail | - | - | - | -
Safe | - | - | - | -
CPT(N = 3)
C₁
C₁
C₁
9

## Slide 10
2 · METHODOLOGY
Proposed Intensity-based DBN
One-top FT
STEP 2
FT Integration & Simplification
Top Event Integration
OR/AND Gates
Figure 4. Traditional ET–FT to proposed DBN conversion (4 steps)
ET–FT to DBN conversion
Intensity-based DBN
STEP 4
Dynamic Intensity Transition
Inter-slice Transition
Damage Factor
ET-FT Model
STEP 1
Accident Scenario & Basic Events
ET Branch Structure
FT Gate Logic
Static BN
STEP 3
CPT-based Probabilistic Structure
Node & Edge Conversion
CPT Construction
10

## Slide 11
Study Area and High Wind Scenarios: Event Tree
Target plant Shin-Kori Units 1 & 2 (OPR1000)
Figure 5. Event tree for high-wind-induced accident scenarios
16 / 20 accident sequences lead to core damage (CD)
2 · METHODOLOGY
11

## Slide 12
Study Area and High Wind Scenarios: Fault Tree
Each initiating event is defined by which structure fails — this is what links fragility to the event tree.
SSC damage → initiating event → consequence
AUX or EDGB
LEP
→ direct core damage
The emergency power itself is destroyed — no mitigation remains.
LEP
(Loss of Essential Power)
EDGB
AUX
ESW or CCW
LOCCW
→ direct core damage
The path to the ultimate heat sink is severed.
LOCCW
(Loss of Component Cooling Water)
CCW
ESW
SWY / TB
LOOP
→ mitigation tree
In-plant safety systems survive: EDG · AFW · SHR · SDC.
LOOP
(Loss of Offsite Power)
TB
SWY
LOOPWBM
(Failure of Switchyard Structure by WBM caused by TB damage)
2 · METHODOLOGY
WBM
Wind-Borne Missile
Figure 6. Fault tree for high-wind-induced accident scenarios
12

## Slide 13
3 · CASE STUDIES & EXTENSION
Case 1: Hazard and Fragility Inputs
① Wind hazard: ΔHi(V)
Data source
Wind-speed return periods, RCP8.5 climate scenario
Hazard curve
Fitted with an extreme-value distribution
Interval (m/s) | 35–40 | 40–45 | 45–50 | 50–55 | 55–60
ΔHi (/yr) | 2.130 E-01 | 3.203 E-02 | 5.987 E-03 | 1.451 E-03 | 3.012 E-04
Table 1. Hazard information: Annual exceedance frequency per wind-speed interval
② SSC fragility — lognormal curves
SSC | vd (m/s) | Fs | Fd | Fp | Vm (m/s)
AUX | 40 | 2.0 | 1.25 | 1.3 | 72.11
EDGB | 40 | 2.0 | 1.25 | 1.3 | 72.11
ESW | 40 | 2.0 | 1.25 | 1.3 | 72.11
CCW | 40 | 2.0 | 1.25 | 1.3 | 72.11
TB | 40 | 2.0 | 1.25 | 1.3 | 72.11
SWY | 36.6 | 1.5 | 1 | 1 | 44.83
Table 2. Fragility parameters (βₑ = 0.1414 for all SSCs)
No damage factor is applied.
The fragility is not modified by any previous damage.
Baseline case
13

## Slide 14
3 · CASE STUDIES & EXTENSION
Case 1: Model Verification
DBN structure built in GeNIe
Figure 7. A DBN built in GeNIe (6 intensity slices)
Interval (m/s) | 35–40 | 40–45 | 45–50 | 50–55 | 55–60
ΔHi (/yr) | 2.130E-01 | 3.203E-02 | 5.987E-03 | 1.451E-03 | 3.012E-04
Table 1. Annual exceedance frequency per wind-speed interval
14

## Slide 15
3 · CASE STUDIES & EXTENSION
Case 1: Model Verification
① EDGB fragility → node CPT
Pf(V) = Φ ( ln( V / Vm ) / β ) Vm = 72.11 m/s, β = 0.1414
Slice | V (m/s) | Pf(EDGB)
0 | 35 | 1.59E-07
1 | 40 | 1.54E-05
2 | 45 | 4.27E-04
3 | 50 | 4.80E-03
4 | 55 | 2.77E-02
5 | 60 | 9.68E-02
Table 3. The CPT of the EDGB node, one entry per intensity slice
② Verification — DBN reproduces ET–FT
V (m/s) | CCDP ET–FT | CCDP DBN
35 | 1.76E-05 | 2.13E-05
40 | 1.51E-04 | 1.70E-04
45 | 1.92E-03 | 1.97E-03
50 | 1.93E-02 | 1.95E-02
55 | 1.04E-01 | 1.07E-01
60 | 3.07E-01 | 3.35E-01
 | 7.94E-05 | 8.23E-05
V (m/s) | CCDP ET–FT | CCDP DBN
35 | 1.76E-05 | 2.13E-05
40 | 1.51E-04 | 1.70E-04
45 | 1.92E-03 | 1.97E-03
50 | 1.93E-02 | 1.95E-02
55 | 1.04E-01 | 1.07E-01
60 | 3.07E-01 | 3.35E-01
 | 7.94E-05 | 8.23E-05
Table 4. CCDP and CDF by wind intensity — ET–FT vs. DBN
Figure 8. The CCDP and dCDF results for high-wind PSA using DBN
LEP
(Loss of Essential Power)
EDGB
AUX
0 1 2 3 4 5
Relative error is 3.7%
15

## Slide 16
3 · CASE STUDIES & EXTENSION
Case 2: Damage State Factor and CPT Update
A damaged structure is weaker against the next wind. The fragility must carry that history.
① The damage state factor, kD
Median capacity is reduced
Vm′ = kD × Vm = 0.9 × 72.11 = 64.90 m/s
kD ∈ (0, 1]. kD = 1.0 is undamaged. A lower kD means more accumulated damage.
Modified fragility
Pf′(V) = Φ ( ln( V / Vm′ ) / β )
② EDGB node CPT — before vs. after
V (m/s) | Case 1 Pf(EDGB) | Case 2 Pf(EDGB) | ratio
35 | 1.59E-07 | 1.59E-07 | —
40 | 1.54E-05 | 1.54E-05 | —
45 | 4.27E-04 | 4.27E-04 | —
50 | 4.80E-03 | 3.26E-02 | 6.8
55 | 2.77E-02 | 1.21E-01 | 4.4
60 | 9.68E-02 | 2.89E-01 | 3.0
Assume EDGB is damaged at V = 50 m/s
Table 5. Updated CPT of the EDGB node
LEP
(Loss of Essential Power)
EDGB
AUX
0 1 2 3 4 5
Figure 9. Comparison of the baseline vs. damaged EDGB fragility
At 60 m/s, the Pf(EDGB) increases approximately 3 times.
16

## Slide 17
3 · CASE STUDIES & EXTENSION
Results: Effect of Damage Propagation
CCDP by wind speed
V (m/s) | Case 1 | Case 2 | ratio
35 | 2.13E-05 | 2.13E-05 | —
40 | 1.70E-04 | 1.70E-04 | —
45 | 1.97E-03 | 1.97E-03 | —
50 | 1.95E-02 | 4.68E-02 | 2.4
55 | 1.07E-01 | 1.92E-01 | 1.8
60 | 3.35E-01 | 4.77E-01 | 1.4
Table 6. Comparison of CCDP between Case 1 and Case 2
dCDF by interval
Interval | ΔH (/yr) | Case 1 (/yr) | Case 2 (/yr)
35–40 | 2.130E-01 | 4.54E-06 | 4.54E-06
40–45 | 3.203E-02 | 5.44E-06 | 5.44E-06
45–50 | 5.987E-03 | 1.18E-05 | 1.18E-05
50–55 | 1.451E-03 | 2.83E-05 | 6.80E-05
55–60 | 3.012E-04 | 3.22E-05 | 5.79E-05
Total CDF |  | 8.23E-05 | 1.48E-04
Table 7. Comparison of dCDF and CDF between Case 1 and Case 2
Figure 10. CCDP comparison · dCDF contribution per interval
The damage factor raises the CCDP about 2.4 times at the 50 to 55 interval.
The total CDF rises about 1.8 times.
Based on this method, once the damage factor is established, it can compute CCDP and CDF from the measured wind speed, in real time.
17

## Slide 18
3 · CASE STUDIES & EXTENSION
Extension: Real-Time Wind-Risk Monitoring
Measured wind speed at the NPP site is fed to the DBN. CCDP and CDF are computed for that intensity, in near real time.
What the screen shows
1
Live wind speed
Measured at the site and pushed to the model on each refresh.
2
Risk curve — CCDP vs. wind speed
The DBN is solved at the measured intensity.
3
Wind-speed history
The measured series over time.
4
CDF trend
Risk accumulated from the hazard curve.
EDGB is damaged above 50 m/s, so the damage state factor is applied. Its median capacity drops to 64.90 m/s, and the CPT of every later slice is updated. The fragility jumps, so the curve shows a step at that point.
1
2
3
4
Figure 11. NPP Wind Hazard Real-Time Risk Monitor
18

## Slide 19
4 · CONCLUSION
Conclusion
This study proposed an intensity-based DBN for high-wind PSA of NPPs.
For this, the high-wind accident scenario was established for Shin-Kori Units 1 and 2.
The proposed method computes CDF as a function of wind intensity. Damage at one intensity level carries into the next through the damage state factor (kD), so the SSC fragility evolves as the wind grows.
In the baseline case, the DBN results were nearly identical to those of the conventional ET–FT method. In the damaged case, with the damage state factor applied, the total CDF increased about 1.8 times.
Future Work
A more accurate and practical assessment requires further study on the damage state factor of each SSC.
The framework can also be extended to the NPP main control room, where the CDF is checked from real-time measured data.
19

## Slide 20
THANK YOU
20