## Slide 1
Internal Flooding Risk Assessment in the Pre-Defueled Phase of BWR/4 Mark I Nuclear Power Plant
Yu-Ting Lin, Po-Jung Chiu, Yi-Cheng Tian, and Tsu-Mu Kao
Presented by
Po-Jung Chiu
Assistant Researcher
PSAM-18
July 20, 2026
National Atomic Research Institute (NARI) | PSAM-18 / 2026
1
Risk Assessment Group, Department of Nuclear Systems Engineering National Atomic Research Institute (NARI), Taiwan

## Slide 2
Presentation Outline
1
Background and objective
2
PD phase plant configuration
3
Internal flooding PRA methodology
4
Qualitative and quantitative screening
5
Dominant scenario and mitigation insight
6
Conclusions
National Atomic Research Institute (NARI) | PSAM-18 / 2026
2

## Slide 3
Why Internal Flooding Matters in the PD Phase
1. Background and Motivation
National Atomic Research Institute (NARI) | PSAM-18 / 2026
3
PD phase configuration
Spent fuel remains in the reactor core; the reactor cavity is hydraulically connected to the SFP.
Cooling dependency
Decay heat removal relies on RHR or SFPACS, depending on plant alignment.
Flooding challenge
Water intrusion can disable electrical distribution and compromise decay heat removal capability.
Objective: develop an Internal Flooding PRA for the decommissioning transition stage and identify risk-significant flood scenarios.

## Slide 4
PD Phase Plant Configuration
2. PD phase plant configuration
National Atomic Research Institute (NARI) | PSAM-18 / 2026
4
Reference plant: BWR/4 Mark I in the decommissioning transition stage.
RPV head removed; refueling cavity maintained at high water level.
RCS is at ambient temperature and atmospheric pressure.
High-energy line break contribution is eliminated for scenario development.
Fuel inventory
Core fuel and SFP fuel are treated as connected risk targets.
Decommissioned sources
Feedwater, main steam, and condensate systems are drained and no longer modeled as flood sources.
Initiating events
PD phase emphasizes loss of decay heat removal; LOOP remains in the model.

## Slide 5
EPRI Internal Flooding PRA Methodology
2. Modeling Framework
National Atomic Research Institute (NARI) | PSAM-18 / 2026
5
Qualitative Evaluation
Tasks 1-4 Flood areas, SSCs, sources, walkdowns, and screening
Quantitative Evaluation
Tasks 5-10 Scenario characterization, IE analysis, consequences, mitigation (HRA), modeling, and quantification
Documentation
Task 11 Traceable technical basis and reproducible PRA records
The same logic is adapted to PD-specific plant conditions and fuel uncovery endpoints.

## Slide 6
Qualitative Screening Logic
2. Modeling Framework
National Atomic Research Institute (NARI) | PSAM-18 / 2026
6
Plant-wide screening excludes buildings or areas with no credible flood source, no safety-significant equipment, or no effective propagation pathway.
Flood-area screening retains areas that may affect core or SFP cooling.
Walkdowns verify source inventory, SSC location, mitigation features, and propagation paths.
A-E
Plant-wide exclusion criteria
F/U/N/D/I
Flood-area impact codes
Propagation
Direct, vertical, or shared drainage pathways
Notes: F: No potential flood sources exist within the area.
U: The area contains no equipment other than cabling. If no propagation pathways exist, the area is screened out.
N: triggers no initiating events relevant to the PRA and involves no safety-related components.
D: The only SSC susceptible to damage is the flood source itself.
I: The area contains equipment critical to the cooling of the reactor core or SFP; these areas are mandatory inclusions for quantitative analysis.

## Slide 7
Quantitative Flood Scenario Modeling
2. Modeling Framework
National Atomic Research Institute (NARI) | PSAM-18 / 2026
7
Flood scenarios include spray, general flooding, major flooding, local inundation, and inter-area propagation.
Scenario consequences are mapped to PRA initiating-event categories.
Fuel Uncover Frequency (FUF) is quantified through the internal event model using OR-gate aggregation.
Human reliability credits operator isolation when time windows are sufficient.
Spray
< 100 gpm
General Flooding
100-2,000 gpm
Major Flooding
> 2,000 gpm
Endpoint
Fuel uncovery in the reactor/SFP connected volume

## Slide 8
Quantitative Screening Results
3. Results and Sensitivity Analysis
National Atomic Research Institute (NARI) | PSAM-18 / 2026
8
Building | Flood Areas | Scenarios | FUF (/yr)
Reactor Building | 14 | 39 | 1.06E-15
Combination Structure | 12 | 33 | 5.04E-07*
Turbine Building | 7 | 18 | 0.00E+00
Service Building | 5 | 15 | 2.20E-16
5th DG | 1 | 6 | 0.00E+00
* Detailed analysis had not yet been conducted at screening stage; the dominant propagated switchgear-room scenario was selected for detailed evaluation.

## Slide 9
Dominant Detailed Scenario:4.16kV Switchgear Room
3. Results and Sensitivity Analysis
National Atomic Research Institute (NARI) | PSAM-18 / 2026
9
Catastrophic failure of a fire protection header in 4.16-kV Switchgear Room B.
Flooding propagates to Switchgear Room A.
Concurrent loss of 4.16-kV buses #1, #2, #3, and #4.
Conditional Fuel Uncovery Probability (CFUP) = 1.0.
Detailed FUF
1.44E-08 / yr
Risk driver
Loss of power distribution directly challenges decay heat removal capability.
Mitigation
Upstream manual isolation valve, normally closed and operated on demand.

## Slide 10
Key Conclusions and Risk Insights
4. Conclusions
National Atomic Research Institute (NARI) | PSAM-18 / 2026
10
PD-phase internal flooding risk is configuration-dependent and differs from power operation.
Quantitative screening covered 36 flood areas and 112 flood scenarios.
The refined plant-level flooding FUF is governed by one switchgear-room propagation scenario.
Targeted configuration control and isolation capability can materially reduce the high-risk profile.
Final plant risk
1.44E-08 / yr
Primary insight
Electrical rooms deserve scenario-based prioritization during PD.
Thank you