## Slide 1: Level 2 PSA Modeling: from Large Event Tree to Integrated Level 1 / Level 2 PSA
PSAM18 – Pittsburgh, July 2026 Shizhen Yu, Iris Juarez, Paul Foucaud

## Slide 2: Content
Introduction
Change of approach
Validation case
Conclusion

## Slide 3: Introduction
Previous Belgian L2 PSA followed large event tree approach as described in NUREG-1150
  In EVNTRE, developed by SNL around 1990
  L1 PSA developed separately in RiskSpectrum
In the current PSR, decided to change to integrated L1 / L2 PSA approach with ET/FT, based on latest US NRC documents on L2 PSA issued in the L3 PRA project*
  In RiskSpectrum
Methodology for L2 PSA development updated, an existing model in EVNTRE rebuilt in RiskSpectrum for benchmarking
* Level 3 Probabilistic Risk Assessment (PRA) Project, Volume 3c: Reactor, At-Power, Level 2 PRA for Internal Events and Floods, 2022
Volume 5b: Reactor, At-Shutdown, Level 2 PRA for Internal Events, 2025

## Slide 4: Change of approach
General considerations:
  Unlike previous generic large event tree approach, integrated approach is dominant sequences dependent
  Preserve a comparable level of details of the model, as far as practically possible

## Slide 5: Change of approach L1 / L2 PSA interface
Large event tree approach
  Transition tree categorizes L1 CD sequences into PDS
  PDS remodeled through the first questions (events) in EVNTRE as starting point of L2 PSA
Integrated L1 / L2 PSA approach
  Input FTs corresponding to the headings/function events of transition tree will be directly linked to L2 FTs
  Attributes not explicitly modelled as function events in transition tree, will be assigned through Boundary Condition Set at the end of the L1 CD sequences

## Slide 6: Change of approach Containment integrity related ET/FT
Large event tree approach
  Cascading event trees to model accident progression and containment integrity, including systems availability, operator actions, accident evolution and phenomena, containment failure modes
Integrated L1 / L2 PSA approach
  1 ET assigning containment integrity status to CD sequences: either intact or certain failure modes
  FTs to remodel all the events in RiskSpectrum

## Slide 7: Change of approach Release categories related ET/FT
Large event tree approach
  Cascading event trees to model FP transport distribution and retention
  Distribution and retention parameters  release categories
Integrated L1 / L2 PSA approach
  1 ET for Early phase and 1 ET for Late phase assigning release categories based on containment status, FP release mitigations…
  FTs for FP release mitigation strategies
  "Additional recovery" to avoid significant Early releases is considered for "slow" sequences: SG feed and bleed, or RWST refilling for RCS injection during extensive time
  Release categories assigned primarily based on representative supporting calculations

## Slide 8: Change of approach Supporting calculations
Large event tree approach
  Base cases without active safety systems for various initiating events
  Variants to consider certain safety systems in the transient to reflect their impact on accident progression
  Calculations tend to be pessimist comparing to dominant PDS
Integrated L1 / L2 PSA approach
  Representative calculations based on dominant CD sequences to cover significant portion of PDS
  CSBO with minimum set of SSCs for severe accident mitigation as bounding case
  Further variants to
    provide phenomenological insights for ET/FT modelling
    support quantification of the release categories
    consider postulated containment failure

## Slide 9: Change of approach Human Reliability Analysis
Large event tree approach
  Based on base cases of supporting calculations
  HRA dependencies implemented through user functions in EVNTRE, which enable dependency consideration directly in result quantification
Integrated L1 / L2 PSA approach
  Based on representative supporting calculations
  At first, quantification considering values without dependency to identify the main MCSs; then, dominant MCSs containing sequential operator actions re-quantified considering dependency

## Slide 10: Change of approach Quantification
Large event tree approach
  Best estimate containment failure frequency and frequencies of different release categories
  Parametric sensitivity analysis for basic events
  No statistical uncertainty analysis
Integrated L1 / L2 PSA approach
  Best estimate containment failure frequency and frequencies of different release categories
  Importance analysis integrating elements from both L1 and L2 FTs to identify high safety significant SSCs regarding L2 risk metrics
  Uncertainty analysis on parameters related to system availability, HRA and phenomena directly impacting containment integrity

## Slide 11: Change of approach Summary of main changes
L1 and L2 models integrated in RiskSpectrum
Containment integrity: 1 ET and events in FTs
Release categories: assigned to branches of ETs, based on representative supporting calculations, which are defined according to dominant CD sequences
State-of-the-art uncertainty and importance analyses

## Slide 12: Validation case
Existing L2 PSA model in EVNTRE rebuilt in RiskSpectrum following integrated approach
Work in progress as some FTs need adaption
Reasonable results for large early releases (released I or Cs > 0.1% inventory until vessel failure)
 | Large event tree | Integrated PSA
% CDF | 1.67 | 1.88

## Slide 13: Conclusion
Methodology for L2 PSA development updated following integrated L1 / L2 PSA approach
EVNTRE model rebuilt in RiskSpectrum, enabling a benchmark to validate the transition
Containment failure frequency and frequencies of different release categories (to be) compared to ensure consistency of results

## Slide 14: Thank you for your attention! shizhen.yu@tractebel.engie.com
Doel NPP – Belgium / © ENGIE ELECTRABEL / Rudy De Barse