## Slide 1: Initiatives to Enhance Generation Safety of Paks NPP
Tamas Siklossy, Attila Bareith, et. al
PSAM18
Pittsburgh, Pennsylvania, USA, July 19-24. 2026
siklossyt@nubiki.hu

## Slide 2: Content
  Motivation and background
  Identification of Single Point Vulnerabilities
    Objectives and scope
    Methodology
    Key findings and lessons learned
  Generation Risk Assessment
    Objectives and scope
    Methodology
    Key findings and lessons learned
  Future plans
  Conclusions

## Slide 3: Motivation and Background
  Four VVER-440 units in operation for ~40 years in Paks (Paks NPP), Hungary
  Ageing -> more frequent corrective maintenance -> generation losses
  Importance of systematically identifying the dominant failure modes leading to generation losses -> enables implementation of targeted measures to enhance plant availability and achieve tangible economic benefits
  PSA methods extended beyond their traditional focus on nuclear safety to support the assessment and management of generation safety
  Two complementary analytical initiatives launched
    Single Point Vulnerability (SPV) identification
    Generation Risk Assessment (GRA)

## Slide 4: SPV Identification – Objectives and Scope
  SPV definition: „Individual component failures that may directly cause an automatic reactor trip or require the operator to immediately shut down the unit” Covers: automatic protection signal-initiated trips + procedure-driven manual shutdowns
  Three categories of SPVs: active / passive /situational (all covered to some extent)
  Goal of SPV program in Paks NPP: eliminate SPVs, or reduce trip risk
  Firs step (Goal of the present work): systematic identification of SPVs

## Slide 5: SPV Identification – Methodology
  Basis: EPRI SPV Guide Rev.2, WANO GL 2019-02 and INPO AP-913
  Methodological framework – three mutually reinforcing approaches:
    Systematic component-by-component review
      Within the equipment reliability program (criticality categorization process)
      System engineering perspective (bottom-up approach)
    Analysis of operating experience
      Review of trip records and event investigation reports from the past ten years
    Targeted evaluation of the PSA (and GRA) model
      Focus: support system dependencies and instrumentation and control interactions
      SPV leads to the occurrence of an initiating event
      Fault tree representation for initiating events - PSA model restructured and supplemented
        IEs – single basic events in internal events PSA, decomposition of IEs is internal hazards PSA
        Evaluation of spurious actuation of plant protection system
    SPV candidates confirmed by multidisciplinary expert panel

## Slide 6: SPV Identification – Key Findings and Lessons Learned
  Results (SPVs identified):
  Method 1 (component-by-component review): initial list established; limited → rev.
  Method 2 (operating experience): 22 SPVs (2 situational), all electrical and I&C comp.
  Method 3 (PSA & GRA model evaluation): 469 SPVs (GRA: 304; PSA: 165)
    Cables: 241 | Contact output devices: 220 | Transmitters: 8
    Single failures may lead to the following initiating events:
      Loss of feedwater pumps
      Inadvertent atmospheric relief valve opening
      RCP intermediate cooling failure
      Loss of both turbine generators
      Inadvertent reactor trip
      Interface LOCA

## Slide 7: GRA – Objectives and Scope
  Quantify likelihood and magnitude of future generation losses primarily due to component failures, in terms of:
    Expected annual frequency of unplanned outages and derates [events/year]
    Annual generation risk, considering restoration time [EFPH/year, MWh/year]
  Identifies dominant risk contributors → supports risk-informed preventive maintenance, capital investment, and plant life time management
  GRA at Paks NPP:
    Focus: balance-of-plant systems (dominant contributors to generation loss)
    To date: 13 BOP systems + 1 safety-related system modelled
    Platform: RiskSpectrum PSA (consistent with nuclear safety PSA)
    Goal: support risk-informed asset management & maintenance activities, identify SPVs

## Slide 8: GRA – Methodology
  Analysis steps:
  System selection and review of basic technological information
  Definition of GRA-related functional failures (i.e. possible deviation from normal operation)
  Event logic model development
    FMECA → fault trees for GRA-related functional failures
    Event trees (to support quantification), where headings collect top events related to the same derate level
    Human reliability analysis (Type A, B, C errors)
    Data analysis (reliability data and repair times from plant PSA or past plant experience)
  Risk quantification and interpretation of results (Unconditional Failure Intensity (W) method)
  Overall framework is consistent with the EPRI GRA methodology; key distinctive features:
  Comprehensive electrical and I&C modelling (detailed electrical circuit analysis for each system)
  Cable failures modelled item-wised based on plant cable registry (ADRIA database)
  -> Spurious actuations modelled comprehensively that goes significantly beyond typical GRA practice

## Slide 9: GRA – Key Findings and Lessons Learned
Exemplary results for the main feedwater system (MFWS)
  GRA-related functional failures:
    Loss of main feedwater pumps → 30% or 100% derate
    Water level increases in HP preheater (spurious actuation) → 3% / 50% / 100% derate
    Spurious control valve closure → 100% derate
    HP preheater pipe rupture → 100% derate
  Aggregate results (all derate levels):
    Annual frequency of generation loss: 6.17×10⁻¹ events/year
    Annual expected generation loss: 1.91×10¹ EFPH | 9.55×10³ MWh
  Dominant contributors: cable failures (water level measurement, control valve cables)
  Good agreement with OPEX (same order of magnitude)
Chart: 
| 100% derate | 50% derate | 30% derate | 3% derate
 | 25.7507 | 0.053199 | 12.083 | 62.113
Chart: 
| 100% derate | 50% derate | 30% derate | 3% derate
 | 85.6309 | 0.049913 | 10.7611 | 3.558

## Slide 10: Future Plans
  SPV program:
    Living program throughout the remaining plant lifetime
    Regular review: (1) operating experience; (2) equipment reliability categorization updates; (3) newly developed GRA models and review PSA and GRA model updates
    Identification of situational SPVs: trip/derate monitor under development
  GRA program:
    Analysis of remaining systems ongoing, when completed:
      Consolidate aggregate generation risk for all modelled systems
      Develop recommendations for improving generation safety
    Model refinements planned:
      Input data review (repair times, cable failure rates, power ascension times)
      More detailed human reliability analysis (erroneous interventions)
      Completeness and modelling uncertainty characterization

## Slide 11: Conclusions
  PSA methods successfully extended to generation safety at Paks NPP
    SPV identification:
      469 potential SPVs found using PSA and GRA
      Dominant types: cables and I&C components
      Combination of the three approaches is essential for prudent identification of SPVs
    GRA:
      13 BOP + 1 safety system modelled
      MWh-based risk metrics provide deeper insights than frequency alone
      Results show good agreement with plant operating experience
      Electrical and I&C components and cables contribute the most to generation risk
  Key cross-cutting lesson: existing PSA model of BOP systems required substantial restructuring and additions for generation safety applications, particularly regarding spurious actuations – more challenging than expected

## Slide 12: Thank you for your attention!