## Slide 1: NRC-RES’ Sitewide, All Hazards Level 3 PRA Project: Approach and Results for Multi-Unit Level 1 Risk
Susan E. Cooper and Alan Kuritzky (USNRC)
18th Probabilistic Safety Assessment and Management (PSAM) Conference
Pittsburgh, Pennsylvania
July 20 - 24, 2026

## Slide 2: Background
USNRC has completed technical work for its sitewide, all hazards Level 3 PRA Project.
In addition to Level 1, 2, and 3 PRAs, the L3PRA project includes an integrated site risk (ISR) task that considers all radiological sources
Integrated site risk (ISR) is defined as the aggregation of risk from all relevant radiological sources
  Two, nearly identical reactors (PWRs)
  Two, hydraulically connected spent fuel pools (SFPs)
  A dry cask storage (DCS) facility
Most experience is for multi-unit (i.e., multiple reactor) PRA
Most relevant guidance addresses multi-unit (MU) PRA:
    IAEA MU PSA guidance (2019, 2023)
    EPRI, “Framework for Assessing MU Risk…” (2021)
Following the 2011 Great Japan Earthquake (and events at Fukushima Daiichi), there has been increased interest in MU risk - both in U.S. and internationally.

## Slide 3: ISR Technical Approach
The technical approach developed to perform ISR included nine (9) steps. At high level, these steps are:
  Sitewide dependency assessment
    MU dependencies
    Dependencies between SFPs and reactors
    Dependencies between DCS and reactors
  Multi-unit (MU) risk estimation
    MU core damage frequency (MUCDF)
    MU release category frequencies (MURCF)
    MU consequences
  Aggregation of MU risk results with spent fuel pool risk
MU risk is addressed first; then multi-source risk.
All hazards (internal and external) were addressed

## Slide 4: Approach to Calculate MUCDF
Cutset estimation method (CEM) approach to calculate MUCDF:
  identify Multi Unit Initiating Events (MUIEs)
  determine the MUIE frequencies (MUIEFs)
  identify cutsets that make up 95 percent of the single unit CDF (SUCDF) for each MUIE
  review cutsets and identify the different basic events (BEs) that need to be addressed to account for MU dependencies
  assign cross-unit BE coupling factors (or hazard correlations) for each relevant cutset
  calculate associated cutset coupling probabilities (as needed)
  calculate MUCDFs
Steps 1, 2, 4 and 5 are identical to the PRA software approach.
Step 3 is unique to CEM approach.
Steps 6 and 7 were performed using Excel spreadsheets with cutsets exported from L3PRA project’s SAPHIRE PRA results.

## Slide 5: Venn Diagram Showing Single Unit (SU), Single Unit Only (SO), and Multi-Unit CDF for Two Units with Dependencies

## Slide 6: Sitewide Dependency Assessment
Used a formal, phased process (based on EPRI, 2021)
  Phase 1: Common initiating events (IEs) (e.g., multi-unit initiating events (MUIEs))
  Phase 2: Shared physical resources, systems, structures, and components (SSCs)
  Phase 3: Identical components, human and organizational dependencies, hazard correlations, proximity dependencies, cascading failures, etc.
Phases and definitions of sitewide dependency categories were similar to those defined in IAEA and EPRI reports on MUPRA

## Slide 7: High Level Results: Sitewide Dependency Assessment
Identified:
  MUIEs (e.g., losses of offsite power (LOOPs), seismic events, loss of service water, high winds) consistent with other studies and guidance
  A few shared resources (e.g., electric power, water supplies) and even fewer shared SSCs
  Many identical components to model as MU common cause failures (CCFs)
  A few fire scenarios that were considered “cascading” events
  Some human and organizational dependencies, mostly relevant for Level 2 PRA only
  Expected hazard correlations for external events
Overall, two units are mostly independent

## Slide 8: High-Level MUCDF Results
Total MUCDF (1.3E-5/rcy) is approximately 10 percent of the total single unit CDF (1.25E-4/rcy)
Contributions to total MUCDF:
  2 percent from all selected internal fire scenarios
  6 percent from wind events
  14 percent from all LOOPs (which also often resulted in station blackout (SBO))
  25 percent from loss of service water
  53 percent from total of all seismic events
Results for FLEX sensitivity cases (which also includes updated RCP seals) are similar to that for SUPRA, e.g.,
  most effective (i.e., ~85 to 95%) for LOOPs, losses of NSCW, and wind events
  much less effective for seismic events (e.g., ~16 – 30% for lower bins; ~2.5% for seismic bin 6; 0% for seismic bins 7 & 8)

## Slide 9: Table 6-3 MUCDF Estimates – Base Case
 | Scenario Name | Scenario Description | MU Scenario Characteristics | MUIEF (/rcy) | MUCDF (/rcy) | % MUCDF (/rcy)
1 | MU-IE-LOOPGR | Grid-related LOOP | SBO and AC power recovery failure | 6.15E-03 | 1.00E-06 | 7.7%
2 | MU-IE-LOOPPC | Plant-centered LOOP | SBO and AC power recovery failure | 1.07E-04 | 1.43E-08 | 0.1%
3 | MU-IE-LOOPSC | Switchyard-centered LOOP | SBO and AC power recovery failure | 2.80E-03 | 3.56E-07 | 2.7%
4 | MU-IE-LOOPWR | Weather-related LOOP | SBO and AC power recovery failure | 2.44E-03 | 4.47E-07 | 3.4%
5 | MU-LONSCW | Loss of NSCW | Loss of NSCW in both units | 3.47E-05 | 3.23E-06 | 24.8%
6 | MU-IE-FRI-1 | MCR abandonment due to fire | Both MCRs are abandoned with CCDP =1 | 1.47E-07 | 1.47E-07 | 1.1%
7 | MU-IE-FRI-2 | Shared (A+Y) area fires by U1 and U2 | at least MU LOOP (assumed) | 3.42E-02 | 2.28E-08 | 0.2%
8 | MU-IE-FRI-3 | U1 to U2 (U1 fires affecting U2) | at least (other unit reactor trip and fire damage) (assumed) | 9.08E-03 | 6.59E-08 | 0.5%
9 | MU-IE-FRI-4 | U2 to U1 (U2 fires affecting U1) | at least (other unit reactor trip and fire damage) (assumed) | 9.08E-03 | 6.59E-08 | 0.5%
10 | MU-IE-EQK-1 | Seismic event in bin 1 (0.1–0.3g) occurs (bin pga 0.17g) | 2-unit SBO due to CCFs in seismic BIN-1 | 1.64E-03 | 8.03E-08 | 0.6%
11 | MU-IE-EQK-2 | Seismic event in bin 2 (0.3–0.5g) occurs (bin pga 0.39g) | 2-unit SBO due to CCFs in seismic BIN-2 | 2.19E-04 | 1.24E-07 | 1.0%
12 | MU-IE-EQK-3 | Seismic event in bin 3 (0.5–0.7g) occurs (bin pga 0.59g) | 2-unit SBO and seismic SSC damage in seismic BIN-3 | 4.79E-05 | 8.24E-07 | 6.3%
13 | MU-IE-EQK-4 | Seismic event in bin 4 (0.7–0.9g) occurs (bin pga 0.79g) | 2-unit SBO and seismic SSC damage in seismic BIN-4 | 1.34E-05 | 1.85E-06 | 14.2%
14 | MU-IE-EQK-5 | Seismic event in bin 5 LOOP (0.9–1.1g) occurs (bin pga 1.0g) | 2-unit SBO and seismic SSC damage in seismic BIN-5 | 4.26E-06 | 2.02E-06 | 15.6%
15 | MU-IE-EQK-6 | Seismic event in bin 6 LOOP (1.1–1.5g) occurs (bin pga 1.29g) | 2-unit SBO and seismic SSC damage in seismic BIN-6 | 1.92E-06 | 1.72E-06 | 13.3%
16 | MU-IE-EQK-7 | Seismic event in bin 7 LOOP (1.5–2.5g) occurs (bin pga 1.94g) | 2-unit SBO and Major structural damage (EQK-BIN7) with CCDP =1 | 2.48E-07 | 2.34E-07 | 1.8%
17 | MU-IE-EQK-8 | Seismic event in bin 8 LOOP (2.5g and above) occurs (bin pga 2.5g) | 2-unit SBO and Major structural damage (EQK-BIN8) with CCDP = 1 | 2.32E-09 | 2.32E-09 | <0.1%
18 | MU-IE-WIND-1 | SBO and SSC wind damage | SBO and WIND damage to SSCs | 8.89E-03 | 7.93E-07 | 6.0%
 |  |  | Total = | 7.47E-02 | 1.30E-05 | 100.0%

## Slide 10: MUCDF Results (continued)
MU dependencies (modeled as coupling factors) play a very important role in the calculated MU risks:
  For weather-related and grid-related LOOPs, cutsets containing MU CCF coupling factors account for 86 percent of MUCDF.
  MU CCFs important contributors to lowest seismic bins
  For seismic bins 5, 6, 7, and 8 (the highest seismic hazard bins):
    MUCDF is 90 to 100 percent of SUCDF.
    For seismic bin 6, cutsets containing MU seismic hazard correlations (e.g., MU coupling factors) account for 97 percent of MUCDF.

## Slide 11: Sitewide dependency contributions to MUCDF for Seismic Bin 6
Chart: 
Chart: Seismic Bin 6
| % CCF1 | % CCF2 | % Random | % Seismic | % Structure | % Other
 | 0 | 0 | 2.3 | 73.7 | 23.5 | 0.5

## Slide 12: Takeaways for MUCDF Results
Only certain IEs affect both reactors simultaneously (e.g., LOOPs, loss of service water, external hazards).
Two reactors on reference site were assessed to be very independent of each other (except for response to large seismic events), e.g.,
  Total MUCDF is only 10 percent of total single unit CDF (SUCDF).
  For LOOPs, MUCDF is less than 10 percent of SUCDF.
  For wind events, MUCDF is less than 1 percent of SUCDF.
MU coupling factors were very important in calculated MU risks, e.g.,
  MU CCF coupling factors very important for LOOPs and lowest seismic bins
  Seismic hazard correlations very important for seismic bins 5, 6, 7, and 8.

## Slide 13
QUESTIONS?

## Slide 14: Sitewide dependency contributions to MUCDF for grid-related LOOPs
Chart: 
| % CCF1 | % CCF2 | % Random
MU-IE-LOOPGR | 85.5 | 14.3 | 0.1
MU-IE-LOOPGR | 85.5 | 14.3 | 0.1

## Slide 15: ISR – Scope, Limitations, and Uncertainties
Because of scope and state-of-the-art limitations, the ISR task is intended to be a “proof of concept,” e.g.,
  Only at-power conditions addressed
    Only internal events low power and shutdown for reactors was addressed by L3PRA project; this limitation could be significant
  Due to computational challenges for NRC’s SAPHIRE PRA code, a simplified approach to develop MU core damage frequencies (MUCDFs) was used
MU Level 2, MU Level 3, and ISR limitations:
  Due to well-known computational challenges for MU Level 2 PRA, MU Level 2 and Level 3 results addressed only:
    Two scenarios: weather-related LOOPs and seismic bin 6 events
    A limited number of MU release category combinations
  Only “base case” addressed because the “FLEX sensitivity” case was not performed for SFPs
Examples of uncertainties:
  Limited data to develop MU common cause failure coupling factors
  Little basis for assignment of MU seismic coupling factors
  Modeling approximations (especially for MU Level 2)